## BOSS Fire Passive Register#1
[8 empty] | NOTE: |  | Only substrates with a "1" in them are an approved tested or assessed system.
System | Service (Tier 1) | Service (Tier 2) | Type - Blank Seal / Linear Joint / Service Penetration / Cavity Barrier | Trade | Service Diameter Range (mm) | Min Dia (mm) | Max Dia (mm) | Element | Original Substrate Tested | Single Layer Fire Rated Plasterboard System BF-XXXX-1 | Double Layer Fire Rated Plasterboard System BF-XXXX-2 | Triple Layer Fire Rated Plasterboard System BF-XXXX-3 | Concrete wall BF-XXXX-4 | Masonry BF-XXXX-5 | Speedpanel / Korok BF-XXXX-6 | AAC / Hebel BF-XXXX-7 | Pronto Panel BF-XXXX-8 | AFS BF-XXXX-9 | Dincel BF-XXXX-10 | Supapanel BF-XXXX-11 | Shaftliner BF-XXXX-12 | 2 layers BOSS Batt - Friction fitted BF-XXXX-13 | 2 layers BOSS Batt - Pattress fitted either side BF-XXXX-14 | Party Wall / IntRwall / Stratawall BF-XXXX-15 | Speedpanel / Korok with Buildup BF-XXXX-16 | AAC / Hebel with Buildup BF-XXXX-17 | Pronto Panel with Buildup BF-XXXX-18 | Supapanel with Buildup BF-XXXX-19 | Shaftliner with Buildup BF-XXXX-20 | Permanent Polymer Formwork BF-XXXX-21 | BOSS Flexi-Batt BF-XXXX-22 | Single layer BOSS Batt BF-XXXX-23 | CLT - Cross Laminated Timber BF-XXXX-24 | Concrete Floor BF-XXXX-25 | AAC / Hebel Floor BF-XXXX-26 | Plasterboard ceiling systems BF-XXXX-27 | Comflor® 60 BF-XXXX-28 | BOSS FlexiBatt™ (Horiz) BF-XXXX-29 | Single layer BOSS Batt (Horiz) BF-XXXX-30 | Double layer BOSS Batt (Horiz) BF-XXXX-31 | Speedpanel / Korok (Horiz) BF-XXXX-32 | CLT (Horiz) BF-XXXX-33 | Substrate Thickness (mm) | Localised build-up required? | Build-up requirement | Fire Stopping Information #1 | Fire Stopping Information #2 | Fire Stopping Information #3 | Fire Stopping Information #4 | Fire Stopping Information #5 | Fire Stopping Information #6 | Annular gap (mm) | Aperture (mm) | Sealant depth (mm) | Sealant Fillet (mm) | Wrap Length (mm) | Product Code | Collar Size / Wrap Product Code | FRL / FRR | Fire Rating | Specimen Size & Details | Report Ref. | Short form reference | Date of Report Issue | Expiry | Reference Standard | Supplementary Standard | Expected Expiry | Additional information | Uniquie drawing reference | 1 layer plasterboard drawing identifier | 2 layer plasterboard drawing reference | 3 layer plasterboard drawing reference | Concrete wall drawing reference | Masonry drawing reference | Speedpanel / Korok drawing reference | AAC / Hebel drawing reference | Pronto Panel drawing reference | AFS drawing reference | Dincel drawing reference | Supapanel drawing reference | Shaftliner drawing reference | 2 layers BOSS Batt - - Friction fitted drawing reference | 2 layers BOSS Batt - Pattress fitted either side drawing reference | Party Wall / IntRwall / Stratawall drawing reference | Speedpanel / Korok with Buildup drawing reference | AAC / Hebel with Buildup drawing reference | Pronto Panel with Buildup drawing reference | Supapanel with Buildup drawing reference | Shaftliner with Buildup drawing reference | Permanent Polymer Formwork drawing reference | BOSS Flexi-Batt drawing reference | Single layer BOSS Batt reference drawing | CLT - Cross Laminated Timber reference drawing | Plasterboard ceiling systems reference drawing | Concrete Floor reference drawing | Speedpanel / Korok (Horiz) reference drawing | AAC / Hebel Floor reference drawing | Single layer BOSS Batt (Horiz) reference drawing | Double layer BOSS Batt (Horiz) reference drawing | BOSS FlexiBatt™ (Horiz) reference drawing | Comflor® 60 reference drawing | CLT (Horiz) reference drawing | Column1 | Column2
BF-2001 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 200 x 200 | 25 | 0 | - | FMHPE | - | -/240/180 | 240 minute | Aperture size of 200 mm x 200 mm. Sealant 25 mm deep in the aperture applied flush with the upper face of the floor and includes a 100 mm deep infill of friction fitted rockwool insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2001 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2002 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 200 x 200 | 30 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Aperture size of 200 mm x 200 mm. Sealant 30mm deep in the aperture applied flush with the upper face of the floor and includes a 100 mm deep infill of friction fitted rockwool insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2002 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2003 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fibre Optic / NBN | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 1.5 | 8 | 0 | 20 | - | FMHPE | - | -/60/60 | 60 minute | Single core 5 mm OD NBN cable. 20 mm × 20 mm fillet on non-exposed side only OR exposed side only. | WF FAS 190335 | CSIRO COT 2921 | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - | The sealant can be installed on either side of the system | BF-2003 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2004 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 15 | 70 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Bundle of 8 Fire Alarm Cables - 2C x 1.5 mm² - Approx Dia ea 10.3 mm. | WF FAS 190335 | SFC FRT 180472b.2 | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2004 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2005 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 15 | 70 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Bundle of 8 Fire Alarm Cables - 2C x 1.5 mm² - Approx Dia ea 10.3 mm. | WF FAS 190335 | SFC FRT 180472b.2 | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2005 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2006 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fibre Optic / NBN | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 8 | - | 0 | 20 | - | FMHPE | - | -/60/60 | 60 minute | Single core 5 mm OD NBN cable. Surface seal around cable and a 20 mm x 20 mm fillet on one side only. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2006 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2007 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fibre Optic / NBN | Service Penetration | Electrical | - | - | - | Wall | 90 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 8 | - | 0 | 20 | - | FMHPE | - | -/60/60 | 60 minute | Single core 5 mm OD NBN cable. Surface seal around cable and a 20 mm x 20 mm fillet on one side only. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2007 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2008 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 20 | 26 | 0 | - | FMHPE | - | -/120/90 | 120 minute | Up to 4 x ELV extra low voltage Fire Alarm cables. Sealant to a depth of 26mm in annular gap and finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2008 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2009 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 30 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 4 x 0.75 mm² TPS (Fire Alarm) Power Cables. Sealant to depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2009 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2010 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 2 x RG6 Coax cables Up to 2 x CAT6 cables, Up to 2 x 4 core security security cable (7/0.20mm) Up to 6 of any type of the above listed cables. Sealant to a depth of 20 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2010 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2011 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 2 x RG6 Coax cables Up to 2 x CAT6 cables, Up to 2 x 4 core security security cable (7/0.20mm) Up to 6 of any type of the above listed cables. Sealant to a depth of 20 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2011 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2012 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 20 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 4 x ELV (extra low voltage) Fire Alarm cables. Sealant to a depth of 25 mm in annular gap and finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2012 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2013 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 30 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 4 x 0.75 mm² TPS (Fire Alarm) Power Cables. Sealant to a depth of 25 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2013 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2014 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 30 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 4 x 0.75 mm² TPS (Fire Alarm) Power Cables. Sealant to a depth of 25 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2014 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2015 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 2 x RG6 Coax cables Up to 2 x CAT6 cables, Up to 2 x 4 core security security cable (7/0.20 mm) Sealant to a depth of 20 mm and finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2015 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2016 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 75 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 38 x Cat6 data cables (50 mm diam.). Sealant to full depth of wall in annular gap finished flush on both sides. Additionally a 13 mm thick FR plasterboard pattress required locally around the service. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2016 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2017 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 75 | 25 | - | FMHPE | - | -/90/90 | 90 minute | Up to 38 x Cat6 data cables (50 mm diam.). Sealant to full depth of wall in annular gap with 25 mm x 25 mm fillet to both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2017 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2018 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 38 x Cat6 data cables. Sealant to a depth of 25 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2018 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2019 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 75 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 38 x Cat6 data cables. Sealant to full depth of wall in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2019 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2020 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Cable bundle of: •Up to 4 x RG6 Coax cables •Up to 4 x Cat6 cables •Up to 2 fire alarm cables •1 x security cable Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2020 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2021 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Cable bundle consisting of: •Up to 2 x RG6 Coax cables •Up to 2 x Cat6 cables •Up to 2 x fire alarm cables •1 x security cable •1 x fig 8 cable Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2021 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2022 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 60 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | Bundle of 8 x 2.5 mm², 2C+E TPS Power Cables. Sealant to depth of plasterboard in annular gap in max. 60 mm aperture finished flush. | WF FAS 190335 | CSIRO COT 2922 | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2022 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2023 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 90 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 60 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | Bundle of 8 x 2.5 mm², 2C+E TPS Power Cables. Sealant to depth of plasterboard in annular gap in max. 60 mm aperture finished flush. | WF FAS 190335 | CSIRO COT 2922 | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2023 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2024 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | - | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | Bundle of 8 x 2.5 mm², 2C+E TPS Power Cables. Sealant to depth of plasterboard in 10 mm annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2024 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2025 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 57 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 6 x 2.5 mm², 2C+E TPS Power Cables. Sealant to depth of plasterboard in 57 mm aperture finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2025 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2026 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 1 x 16 mm² 2C+E Power Cable. Sealant to depth of plasterboard in 40 mm aperture finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2026 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2027 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 57 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 6 x 2.5 mm², 2C+E TPS Power Cables. Sealant to a depth of 25 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2027 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2028 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 57 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 6 x 2.5 mm², 2C+E TPS Power Cables. Sealant to a depth of 25 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2028 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2029 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 20 | 25 | 0 | - | FMHPE | - | -/120/90 | 120 minute | Up to 4 x ELV (extra low voltage) Fire Alarm cables - 2 core round. Sealant to a depth of 25 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2029 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2030 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 20 | 25 | 0 | - | FMHPE | - | -/120/90 | 120 minute | Up to 4 x ELV (extra low voltage) Fire Alarm cables - 2 core round. Sealant to a depth of 25 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2030 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2031 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 1 x 16 mm² 2C+E power cables. Sealant to a depth of 20 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2031 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2032 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 1 x 16 mm² 2C+E power cables. Sealant to a depth of 20 mm and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2032 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2033 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 22 x 2.5 mm², 2C+E TPS Power Cables. Sealant to a depth of 25 mm in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2033 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2034 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 22 x 2.5 mm², 2C+E TPS Power Cables. Sealant to a depth of 25 mm in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2034 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2035 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall with an additional build-up of 13 mm thick FR plasterboard locally around the service | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | Yes |  | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | Full depth | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 22 x 2.5 mm², 2C+E TPS Power Cables. Sealant full depth of the wall in annular gap finished flush on both sides. Wall system to include an additional build-up of 13 mm thick FR plasterboard locally around the service. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2035 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2036 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 90 | Full depth | 25 | - | FMHPE | - | -/90/90 | 90 minute | Up to 22 x 2.5 mm², 2C+E TPS Power Cables. Sealant full depth of the wall in annular gap with 25 mm x 25 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2036 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2037 | Conduit | Conduit Incl. cables | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 70 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 8 x 2.5 mm² 2C+E TPS Power Cables inside a uPVC conduit. Conduit up to 32 mm diameter with wall thickness up to 1.9 mm. Sealant to depth of 20 mm in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2037 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2038 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | - | 44 | 26 | 0 | - | FMHPE | - | -/90/90 - 45 RISF | 90 minute | Up to 4 x 2.5 mm², 2C+E TPS Power Cables. Sealant to full depth of plasterboard ceiling in annular gap finished flush on the underside. BOSS FM300 sealant was also used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. The specimen also achieved RSIF of 55 minutes. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2038 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2039 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 20 | 500 x 20 mm around tray and cables (not base) | 25 | 0 | 600 | FMHPE, FM300 | - | -/120/120 | 120 minute | •10 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, -/120/120, •10 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, -/120/90, •10 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2, -/120/120, •2 × (B) small sheathed (PVC/PVC) 1 × 95 mm2, -/120/120, •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, -/120/120, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, -/120/60, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2, -/120/120. Sealant 25 mm deep in the annular gap around the cables and tray sides only, finished flush. A 300 mm coatback of the cables with BOSS FM-300 to the top side. Cables were installed on a 500 mm tray. For A2, P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2039 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2040 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 180 minute | •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2. Sealant 25 mm deep in annular gap finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2040 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2041 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 120 minute | •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2. Sealant 25 mm deep finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2041 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2042 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | •1 × (D1) large sheathed (PVC/PVC) 4 × 185 mm2, •1 × (D2) large sheathed (EPR/PO) 4 × 185 mm2, •1 × (D3) large sheathed (XLPE/EVA) 4 × 185 mm2. Sealant 25 mm deep in annular gap finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2042 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2043 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 180 minute | •10 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •10 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •10 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2. Sealant 25 mm deep finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2043 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2044 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/240/120 | 240 minute | •100 mm diameter (F) cable bundle (telecommunication cable) (PE/PE) 20 mm x 2 mm x 0.6 mm2 screened. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2044 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2045 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 200 x 200 | 25 | 0 | - | FMHPE | - | -/240/30 | 240 minute | •100 mm diameter (F) cable bundle (telecommunication cable) (PE/PE) 20 mm x 2 mm x 0.6 mm2 screened. Sealant 25mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2045 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2046 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | 160 mm wide x 25 mm high x 1.0 mm thick perforated steel cable tray supporting the following cables: •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2, •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2046 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2047 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 180 minute | •1 × (G1) non-sheathed (wire) (PVC/-) 1 × 95 mm2, •1 × (G2) non-sheathed (wire) (PVC/-) 1 × 185 mm2, Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2047 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2048 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 50 x 50 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/240/120 | 240 minute | •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2048 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2049 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 30 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Up to 6 x 2.5 mm², 2C+E TPS Power Cables. Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2049 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2050 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | •1 × (D1) large sheathed (PVC/PVC) 4 × 185 mm2, •1 × (D2) large sheathed (EPR/PO) 4 × 185 mm2, •1 × (D3) large sheathed (XLPE/EVA) 4 × 185 mm2. Sealant 25 mm deep in annular gap finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2050 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2051 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 180 minute | •10 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •10 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •10 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2. Sealant 25 mm deep finished flush with upper face of floor. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2051 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2052 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/240/120 | 240 minute | •100 mm diameter (F) cable bundle (telecommunication cable) (PE/PE) 20 mm x 2 mm x 0.6 mm2 screened. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2052 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2053 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 200 x 200 | 25 | 0 | - | FMHPE | - | -/240/30 | 240 minute | •100 mm diameter (F) cable bundle (telecommunication cable) (PE/PE) 20 mm x 2 mm x 0.6 mm2 screened. Sealant 25mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2053 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2054 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | 160 mm wide x 25 mm high x 1.0 mm thick perforated steel cable tray supporting the following cables: •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2, •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2054 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2055 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 200 x 200 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/180/120 | 180 minute | •1 × (G1) non-sheathed (wire) (PVC/-) 1 × 95 mm2, •1 × (G2) non-sheathed (wire) (PVC/-) 1 × 185 mm2, Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2055 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2056 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 50 x 50 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/240/120 | 240 minute | •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. P40 MAK Wrap to be installed 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2056 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2057 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 250 x 250 | 25 | 0 | - | FMHPE | - | -/120/90 | 120 minute | System consists of 3 PE pipes; 40 mm x 4.1 mm, 60 mm x 4.0 mm and 125 mm x 7.6 mm, fitted centrally within the aperture. The 60 mm pipe is filled with the following cables: •Up to 3 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •Up to 3 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •Up to 3 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2, •1 × (B) small sheathed (PVC/PVC) 1 × 95 mm2, Sealant 25 mm deep in annular gap finished flush on both sides. The system also includes 100 mm deep infill friction fitted stone wool insulation centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2057 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2058 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 16 mm² 3C+E power cable. Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2058 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2059 | Conduit | Conduit Incl. cables | Service Penetration | Electrical | - | - | - | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 70 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 6 x 2.5 mm² 2C+E TPS Power Cables installed inside a 32mm uPVC Conduit (WT 1.9 mm). Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2059 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2060 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 300 x 100 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | •10 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •10 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •10 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2, •2 × (B) small sheathed (PVC/PVC) 1 × 95 mm2, •Up to 63 mm HDPE pipe. Sealant to depth of plasterboard in annular gap applied in the voids around the cables and pipe in a maximum aperture of 300 mm wide x 100 mm high. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2060 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2061 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 300 x 100 | 75 | 0 | - | FMHPE | - | -/120/120 | 120 minute | •10 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •10 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •10 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2, •2 × (B) small sheathed (PVC/PVC) 1 × 95 mm2, •Up to 63 mm HDPE pipe. Sealant to depth of wall in annular gap applied in the voids around the cables and pipe in a maximum aperture of 300 mm wide x 100 mm high. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2061 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2062 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 15 | 0 | 15 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 65 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 15 mm copper pipe with 13 mm thick Armaflex insulation. Sealant 25 mm deep in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2062 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2063 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 15 | 0 | 15 | Wall | 120 mm thick masonry wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 65 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 15 mm copper pipe with 13 mm thick Armaflex insulation. Sealant 25 mm deep in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2063 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2064 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 125 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 98 | 16 | 35 | 400 | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm copper pipe with 25 mm thick stonewool insulation. Insulation wrapping is extended 400 mm on both sides. Sealant 16mm deep in annular gap and finished with a 35 mm x 35 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2064 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2065 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 125 mm thick masonry wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 125 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 98 | 16 | 35 | 400 | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm copper pipe with 25 mm thick stonewool insulation. Insulation wrapping is extended 400 mm on both sides. Sealant 16mm deep in annular gap and finished with a 35 mm x 35 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2065 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2066 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 164 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | Up to 60 mm copper pipe with 32 mm thick Armaflex insulation. Service is further wrapped with P40 MAK Wrap insulation to 600 mm on both sides. Sealant 25mm deep in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2066 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2067 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 120 mm thick masonry wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 164 | 25 | 0 | 600 | FMHPE, P40MAK | - | -/120/120 | 120 minute | Up to 60 mm copper pipe with 32 mm thick Armaflex insulation. Service is further wrapped with P40 MAK Wrap insulation to 600 mm on both sides. Sealant 25mm deep in annular gap and finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2067 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2068 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 135 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 224 | 16 | 35 | 600 | FMHPE | - | -/120/120 | 120 minute | Up to 100 mm copper pipe with 50 mm thick stonewool insulation. Insulation wrapping is extended 600 mm on both sides. Sealant 26 mm deep in annular gap and finished with 35 mm x 35 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2068 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2069 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 135 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 135 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 224 | 16 | 35 | 600 | FMHPE | - | -/120/120 | 120 minute | Up to 100 mm copper pipe with 50 mm thick stonewool insulation. Insulation wrapping is extended 600 mm on both sides. Sealant 26 mm deep in annular gap and finished with 35 mm x 35 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2069 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2070 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | - | 259 | 25 | 0 | 1000 | FMHPE | - | -/120/120 | 120 minute | Up to 159 mm copper pipe with 32 mm thick glasswool insulation. Insulation wrapping is extended 1000 mm on both sides. Sealant 25 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2070 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2071 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 100 mm thick masonry wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | - | 259 | 25 | 0 | 1000 | FMHPE | - | -/120/120 | 120 minute | Up to 159 mm copper pipe with 32 mm thick glasswool insulation. Insulation wrapping is extended 1000 mm on both sides. Sealant 25 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2071 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2072 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 263 | 25 | 10 | 1000 | FMHPE | - | -/120/120 | 120 minute | Up to 159 mm copper pipe with 32 mm thick Armaflex insulation. Insulation wrapping is extended 1000 mm on both sides. Sealant 25 mm deep in annular gap and finished with a 10 mm x 10 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2072 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2073 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 100 mm thick masonry wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | - | 263 | 25 | 10 | 1000 | FMHPE | - | -/120/120 | 120 minute | Up to 159 mm copper pipe with 32 mm thick Armaflex insulation. Insulation wrapping is extended 1000 mm on both sides. Sealant 25 mm deep in annular gap and finished with a 10 mm x 10 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2073 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2074 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 324 | 0 | 324 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 135 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | 5 | 486 | 26 | 0 | 400 | FMHPE | - | -/90/90 | 90 minute | Up to 324 mm Steel Schedule 40 pipe with 75 mm thick stonewool insulation. Insulation wrapping is extended 400 mm on both sides. 5 mm annular gap sealed on both sides to 26 mm deep. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2074 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2075 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 324 | 0 | 324 | Wall | 135 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 135 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | 5 | 486 | 26 | 0 | 400 | FMHPE | - | -/90/90 | 90 minute | Up to 324 mm Steel Schedule 40 pipe with 75 mm thick stonewool insulation. Insulation wrapping is extended 400 mm on both sides. 5 mm annular gap sealed on both sides to 26 mm deep. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2075 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2076 | Water_Valves_and_Tap Sets |  | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 52 | 0 | 52 | Wall | 2 layers of 13 mm plasterboard both sides, incorporating a baffle of 13 mm FR plasterboard internally on both sides with 12 mm plywood to the opposite side of the service. | - | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 75 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 1-sided installation. System is approved for installation in both directions. Up to 52 mm Uponor water valves with tap unit. Sealant 25 mm deep in annular gap and finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2076 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2078 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 7.5 | Up to 600 x 600 | 15 | 0 | 600 | FMHPE | - | -/60/60 | 60 minute | Up to 40 mm copper pipe with 20 mm thick foil faced glass wool insulation, installed through 100 mm thick double layer of BossBatt in maximum aperture 600 mm x 600 mm. Insulation wrapping is extended 600 mm on both sides. Sealant 15 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2077 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2079 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 7.5 | Up to 600 x 600 | 15 | 0 | 1000 | FMHPE | - | -/60/30 | 60 minute | Up to 159 mm copper pipe with 30 mm thick foil faced glass wool insulation, installed through 100 mm thick double layer of BossBatt in maximum aperture 600 mm x 600 mm. Insulation wrapping is extended 1000 mm on both sides. Sealant 15 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2078 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2080 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 7.5 | Up to 600 x 600 | 100 | 0 | 1000 | FMHPE | - | -/60/60 | 60 minute | Up to 159 mm copper pipe with 30 mm thick foil faced glass wool insulation, installed through 100 mm thick double layer of BossBatt in maximum aperture 600 mm x 600 mm. Insulation wrapping is extended 1000 mm on both sides. Sealant extended to full depth in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2079 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2081 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 7.5 | Up to 600 x 600 | 15 | 0 | 600 | FMHPE | - | -/60/60 | 60 minute | Up to 40 mm steel or iron pipe with 30 mm thick foil faced glass wool insulation, installed through 100 mm thick double layer of BossBatt in maximum aperture 600 mm x 600 mm. Insulation wrapping is extended 600 mm on both sides. Sealant 15 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2080 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2082 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 7.5 | Up to 600 x 600 | 15 | 0 | 1000 | FMHPE | - | -/60/60 | 60 minute | Up to 150 mm steel or iron pipe with 30 mm thick foil faced glass wool insulation, installed through 100 mm thick double layer of BossBatt in maximum aperture 600 mm x 600 mm. Insulation wrapping is extended 1000 mm on both sides. Sealant 15 mm deep in annular gap and finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2081 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2083 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | 10 | - | 16 | 10 | 600 | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm copper pipe with 25 mm thick stonewool insulation. Sealant 16 mm deep in annular gap with a 10 mm x 10 mm fillet both sides. Insulation wrapping is extended 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2082 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2084 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 25-100 | 25 | 100 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | 10 | - | 16 | 10 | 600 | FMHPE | - | -/120/90 | 120 minute | 25 mm - 100 mm copper pipe with 25 mm - 50 mm thick stonewool insulation. Sealant 16 mm deep in annular gap with a 10 mm x 10 mm fillet both sides. Insulation wrapping is extended 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2083 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2085 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | Stonewool insulation | - | - | - | - | 10 | - | 16 | 10 | 600 | FMHPE | - | -/120/90 | 120 minute | Up to 100 mm copper pipe with 50 mm thick stonewool insulation. Sealant 16 mm deep in annular gap with a 10 mm x 10 mm fillet both sides. Insulation wrapping is extended 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2084 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2086 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100-200 | 100 | 200 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | Glasswool insulation | - | - | - | - | 20 | - | 25 | 0 | 600 | FMHPE | - | -/60/30 | 60 minute | 100 mm - 200 mm copper pipe with 32 mm thick glasswool insulation. Sealant 25 mm deep in annular gap both sides, backed with stonewool insulation. Insulation wrapping is extended 600 mm on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2085 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2087 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Up to 32 mm uPVC pipe. Sealant 25 mm deep in annular gap finished flush both sides. The sealant was supported by 10 mm diam. polyethylene backing rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2086 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2088 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Up to 20 mm PEX-Xa pipe. Sealant 25 mm deep in annular gap finished flush both sides. The sealant was supported by 10 mm diam. polyethylene backing rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2087 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2089 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 40 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant 25 mm deep in annular gap finished flush both sides. The sealant was supported by 10 mm diam. polyethylene backing rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2088 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2090 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 x 4 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 40 mm x 4 mm wall thickness PEX pipe. Sealant 25 mm deep in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2089 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2091 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 x 10 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | 110 mm x 10 mm wall thickness PEX pipe. Sealant 25 mm deep in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2090 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2092 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 x 2.1 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 21 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | 50 mm x 2.1 mm wall thickness PP pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2091 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2093 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 x 10.7 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 21 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 110 mm x 10.7 mm wall thickness PP pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2092 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2094 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 x 3.7 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 21 | - | 25 | 0 | - | FMHPE | - | -/30/30 | <60 minute | 110 mm x 3.7 mm wall thickness PP pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2093 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2095 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 x 4.1 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 18.5 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | 40 mm x 4.1 mm wall thickness PE pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2094 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2096 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 7.6 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 13.5 | - | 25 | 0 | - | FMHPE | - | -/60/60 | 60 minute | 125 mm x 7.6 mm wall thickness PE pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2095 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2097 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 11.4 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 13.5 | - | 25 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 125 mm x 11.4 mm wall thickness PE pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2096 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2098 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 x 2 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 18.5 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | 40 mm x 2 mm wall thickness PVC pipe. Sealant 25 mm deep in annular finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2097 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2099 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 114 | 114 | 114 x 3.6 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 25.5 | - | 25 | 0 | - | FMHPE | - | -/90/30 | 90 minute | 114 mm x 3.6 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2098 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2100 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 114 | 114 | 114 x 8.1 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 25.5 | - | 25 | 0 | - | FMHPE | - | -/120/30 | 120 minute | 114 mm x 8.1 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2099 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2101 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 x 3.7 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 50 mm x 3.7 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gap finished flush both sides. The sealant was supported by 10 mm diam. Polyethylene back rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2100 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2102 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 x 2.4 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 50 mm x 2.4 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gap finished flush both sides. The sealant was supported by 10 mm diam. Polyethylene back rods.. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2101 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2103 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 4.8 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/90 | 120 minute | 125 mm x 4.8 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gapfinished flush both sides. The sealant was supported by 10 mm diam. Polyethylene back rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2102 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2104 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 7.4 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 125 mm x 7.4 mm wall thickness PVC pipe. Sealant 25 mm deep in annular gapfinished flush both sides. The sealant was supported by 10 mm diam. Polyethylene back rods. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2103 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2105 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 18.5 | - | 25 | 15 | - | FMHPE | - | -/120/120 | 120 minute | Up to 32 mm cPVC (OD42 mm x 3.4) pipe. Sealant 20 mm depth in annular gapand a 15 mm x 15 mm fillet. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2104 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2106 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 50 mm cPVC (OD60 mm) pipe. Sealant depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2105 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2107 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 0 | - | 0 | 15 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm uPVC pipe. Sealant 15 mm fillet both sides of the wall. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2106 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2108 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm uPVC pipe. Sealant depth of plasterboard in annular gap with and a 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2107 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2109 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 0 | - | 0 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm uPVC pipe. No annular gap. Sealant installedin annular gap with 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2108 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2110 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 32 mm uPVC pipe. Sealant depth of plasterboard in annular gap with and a 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2109 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2111 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 40 mm uPVC pipe. Sealant depth of plasterboard in annular gap finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2110 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2112 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 50 mm uPVC pipe. Sealant depth of plasterboard in annular gap finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2111 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2113 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 80 mm uPVC pipe. Sealant depth of plasterboard in annular gap finished flush on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2112 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2114 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 43 | 0 | 43 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 21.5 | - | 13 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 1-direction sealing installation . System is approved for installation in both directions. Up to 43 mm uPVC pipe. Sealant depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2113 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2115 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/120/120 | 120 minute | Up to 40 x 1.9 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 20 mm annular gap with additional 10 mm × 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2114 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2116 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/60/60 | 60 minute | Up to 125 x 9.2 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 20 mm annular gap with additional 10 mm × 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2115 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2117 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/30/30 | <60 minute | Up to 125 x 1.8 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 20 mm annular gap with additional 10 mm × 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2116 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2118 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 43 | 0 | 43 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 23.5 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 43 mm uPVC pipe. Sealant to depth of plasterboard in 23.5 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2117 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2119 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 16 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Tested Uncapped/Capped - Up to 125 x 4.8 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 16 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2118 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2120 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Tested Uncapped/Capped - Up to 40 x 1.9 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 16 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2119 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2121 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Tested Uncapped/Capped - Up to 40 x 3.0 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 16 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2120 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2122 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 16 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Tested Uncapped/Capped - Up to 125 x 7.4 mm wall thickness uPVC pipe. Sealant to depth of plasterboard in 16 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2121 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2123 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 90 | 0 | 90 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 12.5 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 90 mm HDPE pipe. Sealant to depth of plasterboard in 12.5 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2122 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2124 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 40 mm PP pipe. Sealant to depth of plasterboard in 20 mm annular gap with 10 mm x 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2123 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2125 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/30/30 | <60 minute | Up to 40 mm x 3.7 mm wall thickness PE pipe. Sealant to depth of plasterboard in 20 mm annular gap with 10 mm x 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2124 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2126 | Plastic_Pipes | ABS | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 90 | 0 | 90 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 12.5 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 90 mm ABS pipe. Sealant to depth of plasterboard in 12.5 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2125 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2127 | Plastic_Pipes | ABS | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 10 | - | FMHPE | - | -/120/120 | 120 minute | Up to 40 mm ABS pipe. Sealant to depth of plasterboard in 20 mm annular gap with 10 mm x 10 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2126 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2128 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 5 - 20 mm | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of plasterboard in 5 mm - 20 mm annular gap finished flush both sides. (Pipe can be installed off centre) | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2127 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2129 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 11.5 | - | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PEX/AL/PEX pipe. Sealant to depth of plasterboard in 11.5 mm annular gap with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2128 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2130 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/30 | 120 minute | Up to 25 mm PEX/AL/PEX pipe. Sealant to depth of plasterboard in up to 20 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2129 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2131 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PE-Xb pipe. Sealant to depth of plasterboard in 20 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2130 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2132 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™, BOSS FireMastic-HPE™. | - | - | - | - | - | 3.5 | - | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | Up to 25 mm PE-Xb pipe installed with BOSS 32 mm MaxiCollar on both sides. Sealant 25 mm deep to fill the gap between the collar and pipe on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2131 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2133 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 30 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/- | 120 minute | Up to 32 mm PE-Xb pipe. Sealant to depth of plasterboard in 20 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2132 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2134 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PE-Xb pipe. Sealant to depth of plasterboard in 10 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2133 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2135 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PE-Xb pipe. Sealant to depth of plasterboard in 20 mm annular gap with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2134 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2136 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PE-Xa pipe. Sealant to depth of plasterboard in 10 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2135 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2137 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PE-Xa pipe. Sealant to depth of plasterboard in 20 mm annular gap with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2136 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2139 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 17.5 | - | 13 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 1-sided installation. 1-sided installation. System is approved for installation in to the unexposed side only. Up to 20 mm PE-Xa pipe. Sealant to depth of plasterboard in 17.5 mm annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2137 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2140 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 118 mm wall - Wall incorporated a baffle made of 13 mm FR plasterboard on either side of the wall, in addition to 12 mm plywood fixed to steel angles inside the cavity on the unexposed side. | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 17.5 | - | 25 | 0 | - | FMHPE | - | -/60/60 | 60 minute | 1-sided installation. System is approved for installation in both directions. Up to 20 mm PE-Xa pipe. Sealant to depth of plasterboard in 17.5 mm annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2138 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2141 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 128 mm thick - 1 layer of 25 mm shaftliner on one side and 2 layers of 13 mm plasterboard on the other | - | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 17.5 | - | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 1-sided installation. System is approved for installation in both directions through the double layer plasterboard. Up to 20 mm PE-Xa pipe. Sealant to depth of plasterboard in 17.5 mm annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2139 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2142 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 25 | 10 | - | FMHPE | - | -/120/120 | 120 minute | 1-sided installation. System is approved for installation in both directions. Up to 40 mm x 1.9 mm wall thickness PVC pipe. Sealant to depth of plasterboard in annular gap with 10 mm x 10 mm fillet. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2140 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2143 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | - | 43 | 43 | Wall | 118 mm wall - Wall incorporated a baffle made of 13 mm FR plasterboard on either side of the wall inside the cavity. | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 22.5 | 88 | 26 | 0 | - | FMHPE | - | -/90/90 | 90 minute | 1-sided installation. System is approved for installation in both directions. 43 mm PVC pipe. Sealant to depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2141 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2144 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | - | 43 | 43 | Wall | 13 mm FR plasterboard on the opposite side of the penetration, in addition to 12 mm plywood fixed to steel angles inside the cavity | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 156 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 23.5 | 90 | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 1-sided installation. System is approved for installation in both directions. 43 mm PVC pipe. Sealant to depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2142 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2145 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | - | 43 | 43 | Wall | 128 mm thick - 1 layer of 25 mm shaftliner on one side and 2 layers of 13 mm plasterboard on the other | - | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 6 | - | 26 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 1-sided installation. System is approved for installation in both directions through the double layer plasterboard. 43 mm PVC pipe. Sealant to depth of plasterboard in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2143 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2146 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | Up to 20 mm PEX pipe. Sealant to depth of plasterboard in 20 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2144 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2147 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 16 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 20 mm PEX pipe. Sealant to depth of plasterboard in 20 mm annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2145 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2148 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX pipe. Sealant to depth of plasterboard in 20 mm annular gap finished flush both sides. Pipe can be installed off centre. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2146 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2149 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 20 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PE-Xa pipe. Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2147 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2150 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 11.5 | 48 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PE-Xa pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2148 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2151 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 14 | 60 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 32 mm PE-Xa pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2149 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2152 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2150 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2153 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 5 | 40 | 25 | - | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of 25 mm in annular gap both sides finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2151 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2154 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10 | 40 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2152 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2155 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 11.5 | 48 | 20 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of 20 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2153 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2156 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm PE-Xb pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2154 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2157 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 11.5 | 48 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm PE-Xb pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2155 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2158 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 25.5 | 83 | 20 | 15 | - | FMHPE | - | -/120/120 | 120 minute | cPVC 32 mm (OD42 mm) pipe. Sealant 20 mm depth in annular and a 15 mm x 15 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2156 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2159 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 2 | 24 | Surface only | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 20 mm uPVC pipe. Surface seal only on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2157 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2160 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 7.5 | 40 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 25 mm uPVC pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 mm x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2158 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2161 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20.5 | 73 | 20 | 15 | - | FMHPE | - | -/120/120 | 120 minute | Up to 32 mm uPVC pipe. Sealant to depth of 20 mm in annular gap both sides, with 15 mm x 15 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2159 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2162 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 30-40 | 30 | 40 | Wall | 75 mm thick Hebel wall with an additional build-up of 13 mm thick FR plasterboard locally around the service | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | Yes |  | BOSS FireMastic-HPE™ | - | - | - | - | - | 7 - 2 mm | 44 | 10 | 25 | - | FMHPE | - | -/120/120 | 120 minute | 30 mm - 40 mm uPVC pipe. Sealant to depth of 10 mm in annular gap both sides, with 25 mm x 25 mm fillet both sides. The wall is to be built up with minimum 13 mm thick fire rated plasterboard on one side. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2160 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2163 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 20 mm PEX-A pipe. Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2161 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2164 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20.4 | 0 | 20.4 | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 12.5 | 45 | 25 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 20.4 mm PEX-A pipe. Sealant to depth of 25 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2162 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2165 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 25 | 20 | - | FMHPE | - | -/90/90 | 90 minute | Up to 20 mm PEX/AL/PEX pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2163 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2166 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | 60 | 25 | 20 | - | FMHPE | - | -/90/90 | 90 minute | Up to 20 mm PE-Xb pipe. Sealant to depth of 25 mm in annular gap both sides, with 20 x 20 mm fillet both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2164 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2167 | Plastic_Pipes | Kelox / KeKilit | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 50 | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | 16.5 | 83 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Up to 50 mm OD - Up to 25 mm Kelox plus pipe with 13 mm thick insulation. Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2165 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2168 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 40 mm PEX pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25 mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2166 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2169 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped - Up to 110 mm PEX pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2167 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2170 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 x 2.4 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped - 50 mm x 2.4 mm wall thickness uPVC pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2168 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2171 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 x 3.7 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped - 50 mm x 3.7 mm wall thickness uPVC pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2169 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2172 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 x 4.8 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped - 125 mm x 4.8 mm wall thickness uPVC pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2170 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2173 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 x 7.4 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | 20 | Up to 600 x 600 | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped - 125 mm x 7.4 mm wall thickness uPVC pipe installed through 100 mm thick double layer of BossBatt aperture in separating element, with factory applied BOSS Ablative coating to both faces and PS coating to exposed face. Sealant depth of 25 mm in annular gap finished flush. Maximum aperture 600 mm x 600 mm. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2171 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2174 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 19 | - | 26 | 0 | - | FMHPE | - | -/90/90 - 45 RISF | 90 minute | Up to 25 mm PVC pipe. Sealant to full depth of plasterboard ceiling in annular gap finished flush on the underside. BOSS FM300 sealant was also used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. The specimen also achieved RSIF of 55 minutes. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2172 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2175 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 x 4 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Up to 40 mm x 4 mm wall thickness PEX pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2173 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2176 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 0 | 110 x 10 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/60 | 120 minute | 110 mm x 10 mm wall thickness PEX pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2174 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2177 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-21 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 50 mm PP pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2175 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2178 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 x 10.7 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-21 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 110 mm x 10.7 mm wall thickness PP pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2176 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2179 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 x 3.7 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-21 | - | 25 | 0 | - | FMHPE | - | -/30/30 | <60 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 110 mm x 3.7 mm wall thickness PP pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2177 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2180 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-18.5 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 40 mm PE pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2178 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2181 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 x 7..6 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-13.5 | - | 25 | 0 | - | FMHPE | - | -/60/60 | 60 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 125 mm x 7.6 mm wall thickness PE pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2179 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2182 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 0 | 125 x 11.4 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10-13.5 | - | 25 | 0 | - | FMHPE | - | -/90/90 | 90 minute | Approved for Uncapped/Capped and Capped/Capped - 125 mm x 11.4 mm wall thickness PE pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2180 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2183 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 x 2 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | Up to 18.5 | - | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Approved for Uncapped/Capped and Capped/Capped - Up to 40 mm x 2 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2181 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2184 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 114 | 0 | 114 x 3.6 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 25.5 | - | 25 | 0 | - | FMHPE | - | -/90/30 | 90 minute | Up to 114 mm x 3.6 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2182 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2185 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 114 | 0 | 114 x 8.1 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 25.5 | - | 25 | 0 | - | FMHPE | - | -/120/30 | 120 minute | Up to 114 mm x 8.1 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap finished flush both sides. The system also includes a 100 mm deep infill friction fitted stone wool insulation, centrally located in the annular gap through the floor system. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2183 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2186 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 x 3.7 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 50 mm x 3.7 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2184 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2187 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 x 2.4 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 50 mm x 2.4 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2185 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2188 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 4.8 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/90 | 120 minute | 125 mm x 4.8 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2186 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2189 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 x 7.4 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 20 | - | 25 | 0 | - | FMHPE | - | -/120/120 | 120 minute | 125 mm x 7.4 mm wall thickness PVC pipe. Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2187 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2190 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 3/8" x 5/8" Paircoil with 19 mm thick non fire retardant lagging Up to 2.5 mm² 2C+E TPS Power Cable Sealant to a depth of 25 mm in annular gap and a 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2188 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2191 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | Up to 3/8" x 5/8" Paircoil with 19 mm thick non fire retardant lagging Up to 2.5 mm² 2C+E TPS Power Cable Sealant to a depth of 25 mm in annular gap and a 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2189 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2192 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | - | 80 | 26 | - | - | FMHPE, FM300 | - | -/60/60 | 60 minute | - Paircoil - Up to 10 mm/15 mm insulated copper pipes with non-rated lagging, - Up to 2.5 mm² 2C+E TPS Power Cable, - Up to 1.5 mm² 2 Core Data Cable. - Up to 20 mm uPVC outlet pipe 13 mm plasterboard patch (patress) 150 mm x 150 mm placed over the penetration on both sides, fixed to the wall. The edges of the plasterboard build up coated with a 13 mm x 13 mm fillet of FM300. HPE sealant in the annular gap 26 mm deep finished flush with the wall. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2190 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2193 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ (MC-80) | BOSS FireMastic-HPE™ | - | - | - | - | - | 80 | 13 | 0 | - | MC, FMHPE | MC80 | -/60/60 | 60 minute | - Paircoil - Up to 10 mm/15 mm Insulated Copper Pipes with non-rated lagging, - Up to 2.5mm² 2C+E TPS Power Cable, - Up to 1.5mm² 2 Core Data Cable. Boss MaxiCollar fixed to both sides of the wall. Sealant in the annular gap 13 mm deep finished flush. Sealant also to be applied to the annular gap between the services and collar to the depth of the collar finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2191 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2194 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 16 mm plasterboard both sides, with additional patress for plasterboard | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 124 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | - | 80 | 32 | 10 | - | FMHPE, FM300 | - | -/90/90 | 90 minute | •Paircoil: - Up to 9.5 mm OD Copper Pipes with up to 35.5 mm OD lagging - Up to 15.8 mm OD Copper Pipes with up to 41.1 mm OD lagging. • Nexans Olex WK32 2015 V90 electric cables • Electra cables 2015 EAS7501P cable V-90 RoHS 16 mm plasterboard patch (patress) 150 mm x 150 mm placed over the penetration on both sides, fixed to the wall. The edges of the plasterboard build up coated with a 16 mm x 16 mm fillet of FM300. HPE sealant in the annular gap 26 mm deep with 10 mm x 10 mm fillet. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2192 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2195 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | 1-sided installation. System is approved for installation in to the unexposed side only. - Paircoil - Up to 6.35 mm/9.52 mm Insulated Copper Pipes with non-rated lagging, - Up to 1.5 mm² 2C+E TPS Power Cable - Up to 16 mm PVC flexible outlet pipe. 13 mm deep sealant in annular gap finished flush both sides, backed with a foam backing rod. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2193 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2196 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | 1-sided installation. System is approved for installation in both directions. - Paircoil - Up to 6.35 mm/9.52 mm Insulated Copper Pipes with non-rated lagging, - Up to 1.5 mm² 2C+E TPS Power Cable - Up to 16 mm diameter Polyaire top condition outlet pipe. 13 mm deep sealant in annular gap finished flush both sides, backed with a foam backing rod. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2194 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2197 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | - Paircoil - Polyaire Insulated Copper Pipe, - Up to 1.5 mm² 2C+E TPS Power Cable - Up to 16 mm PVC flexible outlet pipe. Sealant to a depth of 13 mm in annular gap finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2195 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2198 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 26 | 0 | - | FMHPE | - | -/60/60 | 60 minute | - Paircoil - Up to 10 mm/15 mm Insulated Copper Pipes with non-rated lagging, - Up to 2.5 mm² 2C+E TPS Power Cable, - Up to 1.5 mm² 2 Core Data Cable. - Up to 20 mm uPVC conduit outlet pipe. Sealant to a depth of 26 mm in annular gap finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2196 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2199 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ (MC-80) | BOSS FireMastic-HPE™ | - | - | - | - | - | 80 | 13 | 0 | - | MC, FMHPE | MC80 | -/60/60 | 60 minute | - Paircoil - Up to 10 mm/15 mm Insulated Copper Pipes with non-rated lagging, - Up to 2.5 mm² 2C+E TPS Power Cable, - Up to 1.5 mm² 2 Core Data Cable. Boss MaxiCollar fixed to both sides of the wall. Sealant in the annular gap 13 mm deep finished flush. Sealant also to be applied to the annular gap between the services and collar to the depth of the collar finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2197 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2200 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 125 | 25 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Paircoil - Up to 10 mm/16 mm Insulated Copper Pipes insulated with 13 mm thick rubber foam. - Up to 20 mm OD PVC conduit, - Up to 2.5 mm² 2C+E TPS Power Cable, - Up to 1.5 mm² 2 Core Data Cable. Sealant to a depth of 25 mm in annular gap with 25 mm x 25 mm fillet on both sides. Sealant backed with foam backing rod. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2198 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2201 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 100 | 25 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Paircoil - Up to 10 mm/16 mm Insulated Copper Pipes insulated with 13 mm thick rubber foam. - Up to 1.5 mm² 2 Core Data Cable. Sealant to a depth of 25 mm in annular gap with 25 mm x 25 mm fillet on both sides. Sealant backed with foam backing rod. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2199 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2202 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | Up to 125 | 25 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 3 x 20 mm Copper Pipes insulated with Armaflex foamed nitrile rubber wrap - TPS cable - Data cable - Up to 20 mm PVC conduit. Sealant to a depth of 25 mm in annular gap with 25 mm x 25 mm fillet on both sides. Sealant backed with foam backing rod. . | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2200 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2203 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | 1 | 1 | - | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 26 | 10 | - | FMHPE | - | -/90/90 | 90 minute | - Up to 9.5 mm OD Copper Pipes with up to 35.5 mm OD lagging - Up to 15.8 mm OD Copper Pipes with up to 41.1 mm OD lagging, HPE in the annular gap to a depth of 26 mm with a 10 mm x 10 mm surface fillet. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2201 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2204 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 127 | 20 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 3/4" Paircoil with 19 mm thick FR lagging - 0.8 mm / 1.1 mm thick - Up to 1 x 2.5 mm² 3C+E TPS Power Cable - Up to 1 x Cat6 Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.4 mm). Sealant to a depth of 20 mm in annular gap and a 25 mm x 25 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2202 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2205 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 127 | 20 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 5/8" Paircoil with 19 mm thick FR lagging - 0.8 mm / 1.0 mm thick - Up to 1 x 2.5 mm² 3C+E TPS Power Cable - Up to 1 x Cat6 Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.4 mm). Sealant to a depth of 20 mm in annular gap and a 25 mm x 25 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2203 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2206 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 100 | 20 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 5/8" Paircoil with 13 mm thick FR lagging - 0.8 mm / 1.0 mm thick - Up to 1 x 2.5 mm² 3C+E TPS Power Cable - Up to 1 x Cat6 Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.4 mm). Sealant to a depth of 20 mm in annular gap and a 25 mm x 25 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2204 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2207 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 152 | 20 | 25 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 3/4" Paircoil with 19 mm thick FR lagging - 0.8 mm / 1.1 mm thick - Up to 1 x 3/8" x 5/8" Paircoil with 13 mm thick FR lagging - Up to 1 x 32 mm type B copper pipe (WT 1.2 mm) with 25 mm thick lagging Sealant to a depth of 20 mm in annular gap and a 25 mm x 25 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2205 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2208 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 25 | 20 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 5/8" Paircoil with 9 mm thick non-fire rated lagging - 0.8 mm / 1.0 mm thick - Up to 2 x 2.5 mm² 3C+E TPS Power Cable - Up to 2 x Cat6 Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.4 mm). Sealant to a depth of 25 mm in annular gap and a 20 mm x 20 mm fillet on both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2206 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2209 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | 20 | 20 | - | FMHPE | - | -/120/120 | 120 minute | - Up to 1 x 3/8" x 5/8" Paircoil with 9 mm thick FR lagging - Up to 2 x 2.5 mm² 3C+E TPS Power Cable - Up to 2 x Cat6 Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.4 mm). Sealant to a depth of 20 mm in annular and a 20mm x 20mm fillet. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2207 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2210 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 130 mm thick Cross Laminated Timber (CLT) wall system | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 121 | 20 | 0 | - | FMHPE | - | -/90/90 | 90 minute | - Up to 1 x 3/8" x 3/4" Paircoil with 19 mm thick FR lagging - Up to 1 x 2.5 mm² 3C+E TPS Power Cable - Up to 1 x 20 mm uPVC condensate pipe (WT 1.8 mm). - Instrolex control cable Sealant to depth of 20 mm in annular gap both sides, finished flush. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2208 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2211 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ (MC-80) | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 72 | Depth of collar | 0 | - | MC, FMHPE | MC80 | -/90/90 - 45 RISF | 90 minute | - Up to 1 x 3/8 & 5/8 mm Paircoil with 1 mm WT - Up to 1 x 2.5 mm² 2C+E TPS Power Cable - Up to 1 x Cat6 cable - Up to 1 x 25 mm uPVC condensate pipe (WT 2 mm). BOSS MaxiCollar™ installed on the underside of the ceiling around the services. Sealant to fill annular gap between services and the collar to the depth of collar. BOSS FM300 sealant was also used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. The specimen also achieved RSIF of 53 minutes. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2209 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2212 | Conduit | Conduit Incl. cables | Service Penetration | Electrical | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ (MC-80) | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 51 | Depth of collar | 0 | - | MC, FMHPE | MC80 | -/90/90 - 15 RISF | 90 minute | - Up to 2 x 2.5 mm² 2C+E TPS power cables per uPVC conduit, installed in up to a bundle of 2 x 25 mm uPVC condensate pipes (WT 2 mm). BOSS MaxiCollar™ installed on the underside of the ceiling around the services. Sealant to fill annular gap between services and the collar to the depth of collar. BOSS FM300 sealant was also used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. The specimen also achieved RSIF of 24 minutes. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2210 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2213 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 150 | 25 | 0 | - | FMHPE | - | -/240/120 | 240 minute | - Up to 1 1/8" (28.3 mm) copper pipe with 25 mm thick E-Flex ST lagging - Up to 7/8" (22 mm) copper pipe with 25 mm thick E-Flex ST lagging - Up to 1 x 18 mm copper pipe with 19 mm thick lagging - Up to 1 x 20 mm uPVC condensate pipe (WT 1.5 mm). - Up to 2 x 2.5 mm² 3C+E TPS Power Cable - Up to 2 x 2.5 mm² 2C+E TPS Power Cable - Istrolex control cable Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2211 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2214 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 100 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | - Up to 1 x 3/8" x 3/4" Paircoil with 19 mm thick lagging - 1.4 mm / 2.8 mm thick - Up to 1 x 2.5mm² 3C+E TPS Power Cable - Up to 1 x Cat6 Cable - Up to 1 x instrolex control cable - Up to 1 x 2.5mm² 2C+E TPS Power Cable - Up to 1 x 20mm uPVC condensate pipe (WT 1.5mm). Sealant to depth of 25 mm in annular gap to backing rod finished flush both sides. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2212 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2215 | NA |  | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/240/240 | 240 minute | Aperture size of 180 mm x 180 mm. Sealant 25 mm deep in aperture applied flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2213 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2216 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/240/90 | 240 minute | Cable bundle consisting of: •1 × (C1) large sheathed (PVC/PVC) 4 × 95 mm2, •1 × (C2) large sheathed (EPR/PO) 4 × 95 mm2, •1 × (C3) large sheathed (XLPE/EVA) 4 × 95 mm2, •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2214 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2217 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/240/90 | 240 minute | Cable bundle consisting of:' •1 × (D1) large sheathed (PVC/PVC) 4 × 185 mm2, •1 × (D2) large sheathed (EPR/PO) 4 × 185 mm2, •1 × (D3) large sheathed (XLPE/EVA) 4 × 185 mm2. Sealant 25 mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2215 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2218 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/180/30 | 180 minute | Cable bundle consisting of: •5 × (A1) small sheathed (PVC/PVC) 5 x 1.5 mm2, •5 × (A2) small sheathed (EPR/PO) 5 × 1.5 mm2, •5 × (A3) small sheathed (XLPE/EVA) 5 × 1.5 mm2, •1 × (B) small sheathed (PVC/PVC) 1 × 95 mm2, Sealant 25 mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2216 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2219 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/240/30 | 240 minute | •100 mm diameter (F) cable bundle (telecommunication cable) (PE/PE) 20 mm x 2 mm x 0.6 mm2 screened, •2 x 15 mm x 1 mm wall thickness rigid H copper conduits, •2 x 16 mm x 2 mm wall thickness PVC conduits. Sealant 25mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2217 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2220 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 180 x 180 | 25 | 0 | - | FMHPE | - | -/240/60 | 240 minute | •1 × (G1) non-sheathed (wire) (PVC/-) 1 × 95 mm2, •1 × (G2) non-sheathed (wire) (PVC/-) 1 × 185 mm2, Sealant 25 mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA45 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2218 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2221 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 150 mm thick AAC concrete block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 x 50 | 25 | 0 | - | FMHPE | - | -/240/60 | 240 minute | •1 × (E) large sheathed (PVC/PVC) 1 × 185 mm2. Sealant 25 mm deep in annular gap finished flush with both sides of the wall. The sealant backing consisted of 20 mm thick Rockwool RWA4 insulation of density greater than 45 kg/m3. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2219 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2222 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Floor | Comflor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | - | - | - | 100 | 25 | 0 | - | FMHPE, BB-50 | - | -/120/120 | 120 minute | Up to 16 mm paircoil copper pipe with lagging up to 6 mm thick with 25mm uPVC pipe. Sealant to depth of 25 mm in the annular gap finished flush on the top side. Sealant to depth of 25 mm x 20 mm wide recess created in the Batt between the service and batt on the underside, finished flush. When installed in ComFlor 60 (Composite floor deck), 50 mm BOSS batt installed to the underside of the ComFlor floor system within the gap between the top rib and BOSS Batt covered with a trapezoid shape section of BOSS Batt. | WF FAS 190335 | - | 7/072023 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2220 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2224 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 4.5 - 6.5 mm | 110.5 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen #1 achieved 93 minutes integrity 80 mins insulation, but the FRL is limited to the published perfromance of the wall.** 1x 15.5 mm + 9.5 mm Paircoil with 19 mm + 17.5 mm insulation, 1 x TPS cable, 1 x Instrolex control cable, 1 x 20 mm uPVC Condensate drain. Sealant to a depth of plasterboard (13 mm) and finished flush with an additional 15 mm x 15 mm fillet in annular gap. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2221 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2225 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 21 - 22 mm | 60 | 13 | 15 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 20 mm PEX-AL-PEX pipe (DuoPEX Gas pipe). HPE installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2222 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2226 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4.5 - 6 mm | 30 | 13 | 0 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 20 mm PEX pipe (AUSPEX PE-Xb pipe). HPE installed into the annular gap, 13 mm deep finished flush both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2223 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2227 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4.5 - 5 mm | 30 | 13 | 0 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 20 mm PEX-AL-PEX pipe (DuoPEX Gas pipe). HPE installed into the annular gap, 13 mm deep finished flush. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2224 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2228 | Conduit | Conduit Incl. cables | Service Penetration | Electrical | 25 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 6 - 7 mm | 35 | 13 | 15 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 25 mm PVC pipe (NBN P23 Conduit) - MARLEY ARMA PVC Pipe. HPE installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2225 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2229 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | 20.5 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 2 - 4 mm | 24 | 13 | 0 | - | FMHPE | - | -/90/90 | 60 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 2C+E 16 mm2 power cable. HPE installed into the annular gap, 13 mm deep finished flush. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2226 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2230 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4 - 5.5 mm | 26 | 13 | 0 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** Cable bundle 2 x CAT6, 2 x COAX, 1 x Security cable. HPE installed into the annular gap, 13 mm deep finished flush. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2227 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2231 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 43 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 5.5 - 6.5 mm | 55 | 13 | 15 | - | FMHPE | NA | -/90/90 | 90 minute | **Specimen achieved greater perfromance, but the FRL is limited to the published perfromance of the wall.** 32 mm PVC pipe (Harvel ChlorFIT cPVC pipe). HPE installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2228 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2232 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4.5 - 5.5 mm | 36 | 13 | 0 | - | FMHPE | - | -/45/30 | <60 minute | 25 mm PEX pipe (AUSPEX 25 mm PEX pipe). HPE installed into the annular gap, 13 mm deep finished flush both sides. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2229 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2233 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 26 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 5 - 5.5 mm | 36 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 91 minutes, but the FRL is limited to the published perfromance of the wall.** 25 mm PEX-AL-PEX pipe (DuoPEX PEX AL Gas pipe). HPE installed into the annular gap, 13 mm deep finished flush. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2230 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2234 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ (MC-32) | BOSS FireMastic-HPE™ | - | - | - | - | 3 - 4.5 mm | 32 | 13 | 0 | - | MC, FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 91 minutes, but the FRL is limited to the published perfromance of the wall.** 25 mm PEX pipe (AUSPEX 25 mm PEX pipe). HPE installed into the annular gap, 13 mm deep finished flush both sides with a BOSS 32 mm MaxiCollar to both sides. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2231 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2235 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 26 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ (MC-32) | BOSS FireMastic-HPE™ | - | - | - | - | 3 - 4 mm | 32 | 13 | 0 | - | MC, FMHPE | - | -/60/45 | 60 minute | **Specimen achieved 91 minutes, but the FRL is limited to the published perfromance of the wall.** 25 mm PEX-AL-PEX pipe (DuoPEX PEX AL Gas pipe). HPE installed into the annular gap, 13 mm deep finished flush both sides with a BOSS 32 mm MaxiCollar to both sides. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2232 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2236 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 3.5 - 4 mm | 32 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | FRL is limited to the published perfromance of the wall. 1-sided installation. System is approved for installation in both directions - 4 x 2.5 mm², 2C+E TPS Power Cables (Nexans OLEX TPS cable). HPE installed into the annular gap, 13 mm deep finished flush. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2233 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2237 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 6.5 - 7.5 mm | 32 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 91 minutes, but the FRL is limited to the published perfromance of the wall.** 1-sided installation. System is approved for installation in both directions - Cable bundle 2 x CAT6, 2 x COAX, 1 x Security cable. HPE nstalled into the annular gap, 13 mm deep finished flush. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2234 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2238 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 48.5 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 6 - 7 mm | 64 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 90 minutes, but the FRL is limited to the published perfromance of the wall.** 40 mm cPVC Sprinkler pipe. HPE installed into the annular gap, 13 mm deep finished flush. An additional 15x15 fillet both sides. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2235 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2239 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20.5 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4.5 - 5 mm | 30 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 91 minutes, but the FRL is limited to the published perfromance of the wall.** 1-sided installation. System is approved for installation in both directions - 20mm PEX pipe (AUSPEX PEX pipe). . HPE installed into the annular gap, 13 mm deep finished flush. | PF23030-1 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2236 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2243 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 0 - 3 mm | 22 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 93 minutes integrity and insulation, but the FRL is limited to the published perfromance of the wall.** - 2C+E 16 mm² power cable. HPE installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2237 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2244 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 1.5 - 2.5 mm | 20 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 93 minutes integrity and insulation, but the FRL is limited to the published perfromance of the wall.** - 4 x 2C 1.5 mm2 Fire Alarm cable bundle. HPE installed into the annular gap, 13 mm deep finished flush. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2238 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2245 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 4 - 5.5 mm | 30 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 93 minutes integrity and insulation, but the FRL is limited to the published perfromance of the wall.** 1-sided installation. System is approved for installation in both directions - 20 mm PEX-AL-PEX pipe (DuoPEX PEX AL pipe). HPE installed into the annular gap, 13 mm deep finished flush to unexposed side. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2239 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2247 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 6.5 - 8.5 mm | 63 | 13 | 0 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 93 mins integrity 68 mins insulation, but the FRL is limited to the published perfromance of the wall.** 50 mm Steel pipe. HPE installed into the annular gap, 13 mm deep finished flush. An additional 30 mm x 30 mm fillet both sides. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2240 - Same as BF-2236 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2248 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | 7 |  |  | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE | - | - | - | - | - | 1.5 - 2.5 mm | 20 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | **Specimen achieved 93 minutes, but the FRL is limited to the published perfromance of the wall.** 4 x 2C 1.5 mm2 Fire Alarm cable bundle. HPE installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2241 - Same as BF-2237 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2249 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 42 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 2 - 3.5 mm | 46 | 13 | 30 | - | FM300 | NA | -/60/60 | 60 minute | FRL has been limited to the published perfromance of the wall. DN32 Steel pipe. FM 300 installed into the annular gap, 13 mm deep finished flush. An additional 30 mm x 30 mm cone was applied to both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2242 - Same as BF-2239 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2250 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 60 | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 0.5 - 2 mm | 65 | 13 | 30 (Wall) x 50 (pipe) | - | FM300 | NA | -/60/60 | 60 minute | FRL has been limited to the published perfromance of the wall. 50NB Steel pipe. FM 300 installed into the annular gap, 13 mm deep finished flush. An additional 30 mm (Wall) x 50 mm (pipe) fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2243 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2251 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 4.5 - 6 mm | 26 | 13 | 15 | - | FM300 | NA | -/60/60 | 60 minute | FRL has been limited to the published perfromance of the wall. Cable bundle 2 x CAT6, 2 x COAX, 1 x Security cable. FM 300 installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2244 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2252 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 5.5 - 6.5 mm | 32 | 13 | 15 | - | FM300 | NA | -/60/60 | 60 minute | FRL has been limited to the published perfromance of the wall. 4 x 2.5 mm2, 2C+E TPS Power Cables. FM 300 installed into the annular gap, 13 mm deep finished flush. An additional 15 mm x 15 mm fillet both sides. | PF23029 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2245 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2253 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | 0 - 1 mm | 21 | - | - | - | PP-60 | PP-60 | -/15/- | <60 minute | 20 mm PEX pipe. 60 mm BOSS PenoPatch on both sides. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2246 - Same as BF-2245 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2254 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | 0 - 1 mm | 21 | - | - | - | PP-60 | PP-60 | -/60/45 | 60 minute | FRL has been limited to the published perfromance of the wall. 20 mm PEX-AL-PEX pipe (DuoPEX PEX AL pipe). 60 mm BOSS PenoPatch on both sides of the plasterbaord and also wrapped around the service. | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2247 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2255 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 4 - 7.5 mm | 54.5 | 13 | 0 | - | MC, FM300 | - | -/60/60 | 60 minute | FRL has been limited to the published perfromance of the wall. 1-sided installation. System is approved for installation in both directions. - 40 mm uPVC pipe (Marley OPTIM PVC-U pipe). An inverted BOSS 40 mm MaxiCollar with FM300 13 mm deep between the collar and separating element finished flush . | PF23031 | - | 2024-01-09 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2248 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2257 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2249 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2258 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2250 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2259 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe. Sealant 5mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2251 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2260 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2252 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2261 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2253 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2262 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2254 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2263 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2255 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2264 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2256 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2265 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2257 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2266 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2258 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2267 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2259 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2268 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2260 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2269 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2261 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2270 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2262 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2271 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2263 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2272 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2264 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2273 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2265 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2274 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2266 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2275 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2267 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2276 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2268 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2277 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2269 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2278 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2270 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2279 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2271 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2280 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2272 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2281 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2273 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2282 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2274 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2283 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2275 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2284 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2276 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2285 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2277 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2286 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2278 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2287 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2279 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2288 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2280 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2289 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Up to 1100 x 1100 | 5 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. Aperture up to 1100 mm x 1100 mm with 1 layer of BOSS Batt™ pattress fitted over the aperture on both sides with 100 mm overlap of the aperture on all sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2281 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2290 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Steel pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2282 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2291 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Steel pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2283 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2292 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Copper pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2284 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2293 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Copper pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2285 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2294 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32mm Iron pipe. Sealant 25mm deep in 5mm annular gap with 10mm fillet on the top side. P40-MAK Wrap™ 300mm to the top side. Aperture to have minimum 100mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2286 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2295 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | Min 100 mm clearance around pipe | 25 | 10 | 600 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Iron pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2287 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2296 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2288 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2297 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32mm Copper pipe with continuous 30 - 50mm Thermobreak tube lagging. Sealant 25mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300mm to the top side. Aperture to have minimum 100mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2289 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2298 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | MC, BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2290 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2299 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed to the underside. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2291 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2300 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed to the underside, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2292 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2301 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed to the underside. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2293 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2302 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed to the underside, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2294 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2303 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 300 | UW-25, BB-50, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed to the underside. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2295 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2304 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | 5 | Min 100 mm clearance around pipe | 25 | 0 | 600 | UW-25, BB-50, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed to the underside, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. Aperture to have minimum 100 mm clearance around the pipe filled with 2 layers of BOSS Batt™ friction fitted flush with the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2296 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2305 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | BB-50, AC | - | -/120/120 | 120 minute | 100 mm thick double layer of BOSS Batt™ friction fitted into an aperture up to 1100 mm x 1100 mm in size, coated with 1 mm DFT BOSS Ablative Coating™. A bead of sealant is applied to the edges of the batt and the separating element to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2297 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2306 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 100 mm FlexiBatt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FlexiBatt™ | BOSS FlexiCoat-MAK™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | FB-100, FCMAK | - | -/120/120 | 120 minute | 100 mm thick layer of FlexiBatt™ friction fitted into an aperture up to 1100 mm x 1100 mm in size coated with 1 mm DFT BOSS FlexiCoat-MAK™. A bead of sealant is applied to the edges of the batt and the separating element to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2298 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2307 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 100 mm FlexiBatt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FlexiBatt™ | BOSS FlexiCoat-MAK™ | - | - | - | - | - | 200 gap x Unlimited length | 0 | 0 | - | FB-100, FCMAK | - | -/240/180 | 240 minute | 100 mm thick layer of FlexiBatt™ friction fitted into an aperture up to 200 mm gap x Unlimited length coated with 1 mm DFT BOSS FlexiCoat-MAK™. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2299 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2308 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | 200 gap x Unlimited length | Fill Gaps | 0 | - | BB-50, AC | - | -/240/180 | 240 minute | 100 mm thick double layer of BOSS Batt™ friction fitted into an aperture up to 200 mm gap x Unlimited length, coated with 1 mm DFT BOSS Ablative Coating™. A bead of sealant is applied to the edges of the batt and the separating element to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2300 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2309 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | 0 | 20 | 300 | BB-50, FM300, P40MAK | - | -/120/120 | 120 minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray up to 500 mm wide. The tray penetrated 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm and was sealed with a 20 mm x 20 mm fillet of BOSS FireMastic-300™ on both sides. The system was then wrapped with BOSS P40-MAK Wrap for 300 mm on both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2301 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2310 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 100 mm FlexiBatt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FlexiBatt™ | BOSS FlexiCoat-MAK™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | 0 | 20 | 300 | FB-100, FCMAK, FM300, P40MAK | - | -/120/120 | 120 minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray up to 500 mm wide. The tray penetrated a layer of BOSS FlexiBatt™ protecting an aperture up to 1100 mm x 1100 mm and was sealed with a 20 mm x 20 mm fillet of BOSS FireMastic-300™ on both sides. The system was then wrapped with BOSS P40-MAK Wrap for 300 mm on both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2302 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2311 | Power_Cables_Inc_Bundles_and_Trays | Appendix D1 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | 0 | 20 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/120 | 120 minute | Appendix D1 Group A cable configuration, consisting of - 1 single core 630 mm² cable - 1 3C+E 185 mm² cable - 3 3C+E 6 mm² cables - 8 3C+E 16 mm² cables Cable were installed onto a tray up to 500 mm wide. The tray penetrated 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm and was sealed with a 20 mm x 20 mm fillet of BOSS FireMastic-300™ on both sides. The system was then wrapped with BOSS P40-MAK Wrap for 300 mm on both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2303 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2312 | Power_Cables_Inc_Bundles_and_Trays | Appendix D1 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 100 | 20 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Appendix D1 Group A cable configuration, consisting of - 1 single core 630 mm² cable - 1 3C+E 185 mm² cable - 3 3C+E 6 mm² cables - 8 3C+E 16 mm² cables Cable were installed onto a tray up to 500 mm wide. The tray penetrated 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm and was sealed to the full depth of 100mm with a 20 mm x 20 mm fillet of BOSS FireMastic-300™ on both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2304 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2313 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 220 | 0 | 220 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/90/30 | 90 minute | Up to 220 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2305 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2314 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 220 | 0 | 220 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/90/- | 90 minute | Up to 220 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2306 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2315 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/120 | 120 minute | Up to 60 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2307 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2316 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 60 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2308 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2317 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/30 | 120 minute | Up to 159 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2309 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2318 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 159 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2310 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2319 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/30 | 120 minute | Up to 159 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2311 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2320 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 159 | 0 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 159 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2312 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2321 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 600 | BB-50, AC, FM300, P40MAK | - | -/120/90 | 120 minute | Up to 150 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 600 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2313 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2322 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 150 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2314 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2323 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 600 | BB-50, AC, FM300, P40MAK | - | -/120/90 | 120 minute | Up to 150 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 600 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2315 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2324 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 150 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annualar gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2316 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2325 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | BOSS MaxiCollar™ | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK, MC | MC150 | -/120/120 | 120 minute | Up to 80 mm steel pipe with continuous 50 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe and a 150 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2317 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2326 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS MaxiCollar™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | BB-50, AC, FM300, MC | MC150 | -/120/- | 120 minute | Up to 80 mm steel pipe with continuous 50 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm. FireMastic-300™ is applied to any gaps around the pipe and a 150 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2318 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2327 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | BOSS MaxiCollar™ | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK, MC | MC150 | -/120/120 | 120 minute | Up to 80 mm copper pipe with continuous 50 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe and a 150 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2319 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2328 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS MaxiCollar™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | BB-50, AC, FM300, MC | MC150 | -/120/- | 120 minute | Up to 80 mm copper pipe with continuous 50 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm. FireMastic-300™ is applied to any gaps around the pipe and a 150 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2320 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2329 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | BOSS MaxiCollar™ | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK, MC | MC100 | -/120/120 | 120 minute | Up to 50 mm steel pipe with continuous 35 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe and a 100 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2321 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2330 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS MaxiCollar™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/- | 120 minute | Up to 50 mm steel pipe with continuous 35 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm. FireMastic-300™ is applied to any gaps around the pipe and a 100 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2322 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2331 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | BOSS MaxiCollar™ | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK, MC | MC100 | -/120/120 | 120 minute | Up to 50 mm copper pipe with continuous 35 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe and a 100 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2323 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2332 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS MaxiCollar™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/- | 120 minute | Up to 50 mm copper pipe with continuous 35 mm Thermobreak tube lagging, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm. FireMastic-300™ is applied to any gaps around the pipe and a 100 mm BOSS MaxiCollar™ is installed to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2324 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2333 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/120 | 120 minute | Up to 42 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2325 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2334 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 42 mm steel pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annular gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2326 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2335 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | Up to 1100 x 1100 | Fill Gaps | 0 | 300 | BB-50, AC, FM300, P40MAK | - | -/120/120 | 120 minute | Up to 42 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, with P40-MAK Wrap™ insulation 300 mm to both sides. FireMastic-300™ is applied to any gaps around the pipe. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2327 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2336 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | 1 | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | Up to 1100 x 1100 | 10 | 0 | - | BB-50, AC, FM300 | - | -/120/- | 120 minute | Up to 42 mm copper pipe penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1100 mm x 1100 mm, sealed with FireMastic-300™ 10 mm deep in annular gap on both sides, finished flush. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2328 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2337 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 1 layer of 100 mm FlexiBatt™ installed in aperture of designated substrate | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | 1 | - | 100 | None | NA | BOSS FlexiBatt™ | BOSS FlexiCoat-MAK™ | - | - | - | - | - | 200 gap x Unlimited length | 0 | 0 | - | FB-100, FCMAK | - | -/240/180 | 240 minute | 100 mm thick layer of FlexiBatt™ friction fitted into an aperture up to 200 mm gap x Unlimited length coated with 1 mm DFT BOSS FlexiCoat-MAK™. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2329 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2338 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | 1 | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | 200 gap x Unlimited length | Fill Gaps | 0 | - | BB-50, AC | - | -/240/180 | 240 minute | 100 mm thick double layer of BOSS Batt™ friction fitted into an aperture up to 200 mm gap x Unlimited length, coated with 1 mm DFT BOSS Ablative Coating™. A bead of sealant is applied to the edges of the batt and the separating element to both sides. | FAR 4572 | - | 2020-06-26 | 2030-06-26 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2330 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2339 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm PE pipe with 3.0 - 4.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2331 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2340 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 110 mm PE pipe with 10.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2332 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2341 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/60 | 120 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2333 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2342 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 110 mm PE pipe with 2.7 - 10.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2334 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2343 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/120/120 | 120 minute | Up to 125 mm PE pipe with 3.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2335 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2344 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/90/90 | 90 minute | Up to 125 mm PE pipe with 3.1 - 11.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2336 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2345 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC150 | -/120/120 | 120 minute | Up to 160 mm PE pipe with 4.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2337 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2346 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/120/120 | 120 minute | Up to 125 mm PE pipe with 3.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 12.5 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2338 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2347 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC50 | -/120/90 | 120 minute | Up to 50 mm PP/PPR pipe with 2.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2339 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2348 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC50 | -/120/60 | 120 minute | Up to 50 mm PP/PPR pipe with 2.0 - 6.9 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2340 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2349 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/90 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2341 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2350 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/90/90 | 90 minute | Up to 110 mm PP/PPR pipe with 2.7 - 10.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2342 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2351 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/120/90 | 120 minute | Up to 125 mm PP/PPR pipe with 3.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2343 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2352 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/60/60 | 60 minute | Up to 125 mm PP/PPR pipe with 3.1 - 17.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2344 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2353 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC160 | -/90/90 | 90 minute | Up to 160 mm PP/PPR pipe with 4.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2345 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2354 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC160 | -/15/15 | <60 minute | Up to 160 mm PP/PPR pipe with 4.0 - 9.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2346 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2355 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC160 | -/15/15 | <60 minute | Up to 160 mm PP/PPR pipe with 9.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2347 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2356 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC50 | -/120/90 | 120 minute | Up to 50 mm uPVC pipe with 1.8 - 3.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2348 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2357 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 - 6.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2349 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2358 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/120/90 | 120 minute | Up to 125 mm uPVC pipe with 7.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2350 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2359 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC125 | -/90/90 | 90 minute | Up to 125 mm uPVC pipe with 4.8 - 7.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2351 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2360 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, FM300, MC | MC150 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 6.2 - 9.5 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2352 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2361 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 20 | Up to 1200 x 500 | - | 0 | - | BB-50, AC, MC | MC150 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 2.8 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The service included 12 mm thick Armaflex lagging, with a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2353 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2362 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 3 | Up to 1200 x 500 | Depth of collar | 0 | - | BB-50, AC, FMHPE MC | MC32 | -/60/60 | 60 minute | Up to 32 mm PP/PPR pipe with 5.8 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 3 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2354 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2363 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 5 | Up to 1200 x 500 | Depth of collar | 0 | - | BB-50, AC, FMHPE MC | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 5.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2355 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2364 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 5 | Up to 1200 x 500 | Depth of collar | 0 | - | BB-50, AC, FMHPE MC | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 4.5 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2356 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2365 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 5 | Up to 1200 x 500 | Depth of collar | 0 | - | BB-50, AC, FMHPE MC | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 6.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2357 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2366 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 5 | Up to 1200 x 500 | Depth of collar | 0 | - | BB-50, AC, FMHPE MC | MC65 | -/60/30 | 60 minute | Up to 50 mm cPVC pipe with 10.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2358 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2367 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 144 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 5 | Up to 1200 x 500 | 10 | 0 | - | BB-50, AC, MC | MC100 | -/120/120 | 120 minute | 100 mm uPVC pipe with 3.2 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 144 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2359 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2368 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 75 mm thick rigid walls. | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 15 | Up to 1200 x 500 | 5 | 0 | - | BB-50, AC, FM300, MC | MC40 | -/120/90 | 120 minute | Up to 40 mm uPVC pipe with 3.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 5 mm deep in 15 mm annular gap finished flush both sides. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2360 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2369 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 75 mm thick rigid walls. | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 13 | Up to 1200 x 500 | 5 | 0 | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 5 mm deep in 13 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2361 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2370 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 75 mm thick rigid walls. | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | 0 | - | BB-50, AC, FM300, MC | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 3.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 5 mm deep in 11 mm annular gap finished flush both sides. The system includes a 80 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2362 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2371 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 75 mm thick rigid walls. | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10.5 | Up to 1200 x 500 | 5 | 0 | - | BB-50, AC, FM300, MC | MC100 | -/120/- | 120 minute | Up to 100 mm uPVC pipe with 3.8 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed around service 5 mm deep in 10.5 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2363 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2372 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2364 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2373 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2365 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2374 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2366 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2375 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2367 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2376 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2368 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2377 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2369 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2378 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2370 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2379 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2371 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2380 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2372 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2381 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2373 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2382 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2374 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2383 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2375 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2384 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2376 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2385 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2377 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2386 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2378 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2387 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | 20 - 50 | Up to 1100 x 1100 | 25 | 50 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2379 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2388 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 with 2nd layer 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | Power Cables: A1 – PVC/PVC 5mm x 1.5mm² - Approx. Dia 14mm A1 – EPR/PO 5mm x 1.5mm² - Approx. Dia 11.2-14.4mm A1 – XLPE/EVA 5mm x 1.5mm² - Approx. Dia 13mm B – PVC/PVC 1mm x 95mm² - Approx. Dia 18-21mm D1 – PVC/PVC 4mm x 185mm² - Approx. Dia 52mm D2 – EPR/PO 4mm x 185mm² - Approx. Dia 64-80mm D3 – XLPE/EVA 4mm x 185mm² - Approx. Dia 58mm FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2380 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2389 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Power Cables: A1 – PVC/PVC 5mm x 1.5mm² - Approx. Dia 14mm A1 – EPR/PO 5mm x 1.5mm² - Approx. Dia 11.2-14.4mm A1 – XLPE/EVA 5mm x 1.5mm² - Approx. Dia 13mm B – PVC/PVC 1mm x 95mm² - Approx. Dia 18-21mm D1 – PVC/PVC 4mm x 185mm² - Approx. Dia 52mm D2 – EPR/PO 4mm x 185mm² - Approx. Dia 64-80mm D3 – XLPE/EVA 4mm x 185mm² - Approx. Dia 58mm FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2381 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2390 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 with 2nd layer 300 | BB-50, TDW, FM300, TD | - | -/120/120 | 120 Minute | Telecommunications Cables: G1 – PVC/- 1mm x 95mm² - Approx. Dia 14.1-17.1mm G2 – PVC/- 1mm x 185mm² - Approx. Dia 19.3-23.3mm FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2382 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2391 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 50 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | Telecommunications Cables: G1 – PVC/- 1mm x 95mm² - Approx. Dia 14.1-17.1mm G2 – PVC/- 1mm x 185mm² - Approx. Dia 19.3-23.3mm FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2383 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2392 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2384 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2393 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2385 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2394 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2386 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2395 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25 TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2387 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2396 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2388 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2397 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2389 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2398 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2390 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2399 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25 TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2391 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2400 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 250 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2392 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2401 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2393 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2402 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 250 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2394 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2403 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2395 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2404 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2396 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2405 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2397 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2406 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2398 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2407 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25 TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2399 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2408 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2400 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2409 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2401 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2410 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2402 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2411 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2403 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2412 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 250 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2404 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2413 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2405 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2414 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 250 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2406 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2415 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100mm thick walls. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2407 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2416 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2408 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2417 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2409 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2418 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2410 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2419 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25 TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2411 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2420 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2412 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2421 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2413 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2422 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2414 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2423 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2415 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2424 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 250 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2416 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2425 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2417 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2426 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 250 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2418 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2427 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FM300, UW-25 TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2419 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2428 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2420 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2429 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2421 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2430 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2422 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2431 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25 TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2423 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2432 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2424 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2433 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2425 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2434 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2426 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2435 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2427 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2436 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 250 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2428 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2437 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2429 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2438 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 250 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2430 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2439 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 0 | 600 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2431 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2440 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2432 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2441 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2433 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2442 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2434 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2443 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2435 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2444 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2436 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2445 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2437 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2446 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2438 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2447 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2439 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2448 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2440 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2449 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2441 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2450 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2442 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2451 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | Up to 20 | Up to 1100 x 1100 | 25 | 20 | 600 with 2nd layer 300 | BB-50, AC, FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2443 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2452 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 50 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2444 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2453 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 16 | 50 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 16mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2445 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2454 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 50 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2446 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2455 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 16 | 50 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 16mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2447 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2456 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 50 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2448 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2457 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 25 | 50 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2449 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2458 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 | FM300, TDW | - | -/120/120 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2450 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2459 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 25 | 50 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireMastic-300™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2451 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2460 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 50 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2452 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2461 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 16 | 50 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 16mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2453 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2462 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 50 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2454 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2463 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 16 | 50 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2455 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2464 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2456 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2465 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 25 | 50 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | Cable bundle -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2457 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2466 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2458 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2467 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | 20 - 50 | - | 25 | 50 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a tray minimum 300 mm wide. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap. For annular gaps larger than 20mm and up to 50 mm, a mineral wool backing rod must be used to back the applied sealant. The service is to be finished with a 50 mm x 50 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2459 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2468 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 with 2nd layer 300 | FM300, TDW | - | -/120/120 | 120 Minute | Power Cables: A1 – PVC/PVC 5mm x 1.5mm² - Approx. Dia 14mm A1 – EPR/PO 5mm x 1.5mm² - Approx. Dia 11.2-14.4mm A1 – XLPE/EVA 5mm x 1.5mm² - Approx. Dia 13mm B – PVC/PVC 1mm x 95mm² - Approx. Dia 18-21mm D1 – PVC/PVC 4mm x 185mm² - Approx. Dia 52mm D2 – EPR/PO 4mm x 185mm² - Approx. Dia 64-80mm D3 – XLPE/EVA 4mm x 185mm² - Approx. Dia 58mm FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2460 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2469 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 with 2nd layer 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | Power Cables: A1 – PVC/PVC 5mm x 1.5mm² - Approx. Dia 14mm A1 – EPR/PO 5mm x 1.5mm² - Approx. Dia 11.2-14.4mm A1 – XLPE/EVA 5mm x 1.5mm² - Approx. Dia 13mm B – PVC/PVC 1mm x 95mm² - Approx. Dia 18-21mm D1 – PVC/PVC 4mm x 185mm² - Approx. Dia 52mm D2 – EPR/PO 4mm x 185mm² - Approx. Dia 64-80mm D3 – XLPE/EVA 4mm x 185mm² - Approx. Dia 58mm FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2461 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2470 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 with 2nd layer 300 | FM300, TDW | - | -/120/120 | 120 Minute | Telecommunications Cables: G1 – PVC/- 1mm x 95mm² - Approx. Dia 14.1-17.1mm G2 – PVC/- 1mm x 185mm² - Approx. Dia 19.3-23.3mm FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2462 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2471 | Data_Comms_Cables_Inc_Bundles_and_Trays | Telecommunications | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 50 | 600 with 2nd layer 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | Telecommunications Cables: G1 – PVC/- 1mm x 95mm² - Approx. Dia 14.1-17.1mm G2 – PVC/- 1mm x 185mm² - Approx. Dia 19.3-23.3mm FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 50 mm x 50 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2463 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2472 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 300 | FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2464 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2473 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2465 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2474 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2466 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2475 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2467 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2476 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 300 | FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2468 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2477 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2469 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2478 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2470 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2479 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2471 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2480 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 250 | FM300, TDW | - | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2472 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2481 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FM300, TDW | - | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2473 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2482 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 250 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2474 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2483 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2475 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2484 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 300 | FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2476 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2485 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2477 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2486 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2478 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2487 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2479 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2488 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 300 | FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2480 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2489 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2481 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2490 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2482 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2491 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2483 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2492 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 250 | FMEMA, TDW | - | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2484 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2493 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 16 | 20 | 600 | FMEMA, TDW | - | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 16mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2485 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2494 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 250 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2486 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2495 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 1 layer 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 16 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/90/90 | 90 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2487 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2496 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 300 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2488 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2497 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2489 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2498 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2490 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2499 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2491 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2500 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 300 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2492 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2501 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2493 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2502 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2494 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2503 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2495 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2504 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 250 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2496 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2505 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FM300, TDW | - | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2497 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2506 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 250 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2498 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2507 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2499 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2508 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2500 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2509 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2501 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2510 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2502 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2511 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2503 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2512 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2504 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2513 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2505 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2514 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-113 | 32 | 113 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 113mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 300mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2506 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2515 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 113-159 | 113 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 113mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2507 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2516 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 250 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2508 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2517 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 | FMEMA, TDW | - | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2509 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2518 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-54 | 32 | 54 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 250 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 54mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 250mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2510 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2519 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 54-159 | 54 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | As required | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 0 | 600 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 54mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. 600mm of Thermal Defence Wrap each side of the wall. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2511 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2520 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2512 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2521 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2513 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2522 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2514 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2523 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Steel pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2515 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2524 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2516 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2525 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2517 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2526 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2518 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2527 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Iron pipe with maximum wall thickness of 4.5mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2519 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2528 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireMastic-300™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2520 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2529 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FM300, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireMastic-300™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2521 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2530 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | - | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, TDW | - | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. FireSilicone-EMA™ Sealant installed 25mm deep in annular gap up to 20mm wide, finished with a 20 mm x 20 mm fillet on the top side. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2522 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2531 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | BOSS Thermal Defence Wrap | BOSS UniWrap™ | - | - | - | Up to 20 | - | 25 | 20 | 600 with 2nd layer 300 | FMEMA, UW-25, TDW | Up to 12 Layers UW-25 | -/120/120 | 120 Minute | 32mm - 159mm Copper pipe with maximum wall thickness of 1.0mm. 30 - 50 mm lagging. UniWrap™ installed over the Thermobreak lagging with multiple layers, flush on both sides to a minimum 40mm depth. FireSilicone-EMA™ Sealant installed in annular gap flush on both sides. Thermal Defence Wrap on the top side of the floor with a 600mm 1st layer and 300mm 2nd layer. | WF FAS 200332 | - | 2020-12-04 | 2025-12-31 | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2523 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2532 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2524 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2533 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2525 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2534 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe. Sealant 5mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2526 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2535 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2527 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2536 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2528 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2537 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2529 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2538 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2530 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2539 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2531 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2540 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 -159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 5 | 0 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe. Sealant 5 mm deep in 5 mm annular gap both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2532 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2541 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2533 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2542 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2534 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2543 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2535 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2544 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2536 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2545 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2537 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2546 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2538 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2547 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2539 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2548 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2540 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2549 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/90/90 | 90 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2541 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2550 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2542 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2551 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2543 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2552 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2544 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2553 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2545 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2554 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2546 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2555 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/90/90 | 90 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2547 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2556 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2548 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2557 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2549 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2558 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 -80 | 32 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 300 | UW-25, FM300, P40MAK | 9 layers of UW-25 | -/120/120 | 120 minute | 32 mm - 80 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 300 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2550 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2559 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2551 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2560 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2552 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2561 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/90/90 | 90 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2553 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2562 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2554 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2563 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2555 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2564 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 80-159 | 80 | 159 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts, fire-rated plasterboard, calcium silicate board, or Shaftliner board. | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 5 | 0 | 600 | UW-25, FM300, P40MAK | 12 layers of UW-25 | -/120/120 | 120 minute | 80 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 5 mm deep in 5 mm annular gap both sides. BOSS UniWrap™ installed on both sides. P40-MAK Wrap™ 600 mm to both sides. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2556 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2565 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Steel pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2557 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2566 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Steel pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2558 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2567 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Copper pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2559 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2568 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Copper pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2560 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2569 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 300 | FM300, P40MAK | - | -/120/120 | 120 minute | 32mm Iron pipe. Sealant 25mm deep in 5mm annular gap with 10mm fillet on the top side. P40-MAK Wrap™ 300mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2561 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2570 | Metal_Pipes | Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 5 | - | 25 | 10 | 600 | FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm - 159 mm Iron pipe. Sealant 25 mm deep in 5 mm annular gap with 10 mm fillet on the top side. P40-MAK Wrap™ 600 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2562 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2571 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2563 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2572 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32mm Copper pipe with continuous 30 - 50mm Thermobreak tube lagging. Sealant 25mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2564 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2573 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | MC, FM300, P40MAK | - | -/120/120 | 120 minute | 32 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. BOSS MaxiCollar™ installed on the underside. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS MaxiCollar TDS to determine the appropriate collar sizes for the relevant pipe diameter. | BF-2565 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2574 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | UW-25, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed mid-depth of the floor. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2566 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2575 | Insulated_Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 600 | UW-25, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Steel pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed mid-depth of the floor, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2567 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2576 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | UW-25, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed mid-depth of the floor. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2568 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2577 | Insulated_Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 600 | UW-25, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Copper pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed mid-depth of the floor, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2569 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2578 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 300 | UW-25, FM300, P40MAK | 2 Layers UW-25 | -/120/120 | 120 minute | 32 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. 2 layers of BOSS UniWrap™ installed mid-depth of the floor. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2570 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2579 | Insulated_Metal_Pipes | Insulated Iron Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32-159 | 32 | 159 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | 5 | - | 25 | 0 | 600 | UW-25, FM300, P40MAK | Up to 12 Layers UW-25 | -/120/120 | 120 minute | 32 mm - 159 mm Iron pipe with continuous 30 - 50 mm Thermobreak tube lagging. Sealant 25 mm deep in 5 mm annular gap both sides. Up to 12 layers of BOSS UniWrap™ installed mid-depth of the floor, depending on pipe size. P40-MAK Wrap™ 300 mm to the top side. | WF FAS 190346 | - | 2021-08-04 | 2025-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Please refer to the referenced report and the BOSS UniWrap TDS to determine the appropriate installation details for the relevant pipe diameter. | BF-2571 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2580 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/300/300 | 300 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the wall face, installed on one side only of a 250 mm thick masonry wall system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2572 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2581 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 30 wide | 15 | - | - | FM300 | - | -/300/180 | 300 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with the wall face, installed on one side only of a 250 mm thick masonry wall system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2573 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2582 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/300/180 | 300 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the wall face, installed on one side only of a 250 mm thick masonry wall system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2574 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2583 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick masonry wall to rigid mild steel | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 30 wide | 15 | - | - | FM300 | - | -/300/90 | 300 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with the wall face, installed on one side only of a 250 mm thick masonry wall to rigid mild steel system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2575 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2584 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/300/120 | 300 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 250 mm thick concrete floor system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2576 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2585 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 30 wide | 15 | - | - | FM300 | - | -/300/60 | 300 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 250 mm thick concrete floor system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2577 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2586 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/300/180 | 300 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 250 mm thick concrete floor system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2578 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2587 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/120/45 | 120 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2579 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2588 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall to softwood timber | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/30/15 | <60 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall to softwood timber system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2580 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2589 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall to rigid mild steel | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/120/15 | 120 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall to rigid mild steel system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2581 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2590 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/240/45 | 240 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2582 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2591 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor to softwood timber | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/30/30 | <60 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor to softwood timber system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2583 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2592 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor to rigid mild steel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 20 wide | 10 | - | - | FM300 | - | -/240/30 | 240 minute | Linear gap seal up to 20 mm wide, with 10 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor to rigid mild steel system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2584 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2593 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/45/45 | <60 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall to softwood timber system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2585 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2594 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/45/30 | <60 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall to rigid mild steel system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2586 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2595 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 100 mm thick masonry wall | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/120/60 | 120 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the wall face, installed on one side only of a 100 mm thick masonry wall system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2587 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2596 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/240/90 | 240 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2588 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2597 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor to rigid mild steel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/240/90 | 240 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor to rigid mild steel system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2589 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2598 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor to softwood timber | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | Up to 50 wide | 25 | - | - | FM300 | - | -/45/45 | <60 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the underside of the floor face, installed on one side only of a 150 mm thick concrete floor to softwood timber system gap. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2590 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2599 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | - | Full depth of plasterboard | - | - | FM300 | - | Up to 300 minutes | 300 minute | Perimeter edge gap seal up to 10 mm wide. Sealant to be applied to the full depth of the plasterboard layer/s, and backed by timber or steel framing with its interface to a concrete wall. The FRL is relative the to the stated perfromance of the wall system. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2591 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2600 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | - | Full depth of plasterboard | - | - | FM300 | - | Up to 300 minutes | 300 minute | Perimeter edge gap seal up to 20mm wide to a deflection head track. Sealant to be applied to the full depth of the plasterboard layer/s, and backed by steel framing with its interface to a concrete wall. The FRL is relative the to the stated perfromance of the wall system. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2592 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2601 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | - | Full depth of plasterboard | - | - | FM300 | - | Up to 300 minutes | 300 minute | Perimeter of the wall system sealed at the interface of the concrete wall with a bead of sealant. Where a C-Track is fixed to the wall, a bead of sealant can be applied between the wall and C-Track. The FRL is relative the to the stated perfromance of the wall system. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2593 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2602 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | Generic substrate | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | No greater than 5 | - | Fill gaps | - | - | FM300 | - | Up to 300 minutes | 300 minute | Intumescent damper, face fixed to the wall system - Sealant applied to the section of damper in contact with the wall and to any steel brackets attached to the wall. The damper must overlap the wall by at least 50 mm and any gaps must not exceed 5 mm. The FRL is relative the to the stated perfromance of the system. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - | Damper manufacturer’s installation instructions must be followed in accordance with the requirements for the specific separating element and the necessary FRL rating. | BF-2594 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2603 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | Generic substrate | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | No greater than 5 | - | Fill gaps | - | - | FM300 | - | Up to 300 minutes | 300 minute | Intumescent damper, in-line with the wall system - Sealant applied to all edges of the damper, with gaps not exceeding 5 mm, filled to the full depth of the damper. The FRL is relative the to the stated perfromance of the system. | FAR 3821 | - | 2022-08-16 | 2032-08-16 | AS 1530.4:2014 | AS 4072.1-2005 | - | Damper manufacturer’s installation instructions must be followed in accordance with the requirements for the specific separating element and the necessary FRL rating. | BF-2595 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2604 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ - Installed in 150 mm AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | Up to 200 x unlimited length | - | - | - | BB-50, AC | - | -/60/60 | 60 minute | 1 layer of 50 mm thick BOSS Batt™ (140 kg/m3) friction fitted to the upper face of a 200 mm wide aperture within the floor system, up to unlimited length. Batt to be coated on both faces with BOSS Ablative Coating™. | FAR 3921.3 | - | 2022-08-16 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2596 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2605 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 1 layer of 100 mm BOSS FlexiBatt™ - Installed in 150 mm AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FlexiBatt™ | BOSS FlexiCoat-MAK™ | - | - | - | - | - | Up to 200 x unlimited length | - | - | - | FB-100, FCMAK | - | -/120/120 | 120 minute | 1 layer of 100 mm thick BOSS FlexiBatt™ (80 kg/m3) friction fitted to the upper face of a 200 mm wide aperture within the floor system, up to unlimited length. Batt to be coated on both faces with BOSS FlexiCoat-MAK™. | FAR 3921.3 | - | 2022-08-16 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2597 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2606 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ - Installed in 150 mm AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | Up to 1600 x 700 | - | - | - | BB-50, AC | - | -/60/60 | 60 minute | 1 layer of 50 mm thick BOSS Batt™ (140 kg/m3) friction fitted to the upper face of a 1600 mm long x 700 wide aperture within the floor system. Batt to be coated on both faces with BOSS Ablative Coating™. | FAR 3921.3 | - | 2022-08-16 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2598 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2607 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 12 | 6 | - | - | FMEMA | - | -/180/120 | 180 minute | Linear gap seal up to 12 mm wide, with 6 mm deep sealant applied flush with the top face of the floor, backed by a 13 mm PEF backing rod. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2599 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2608 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 30 | 15 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with the top face of the floor, backed by a 30 mm PEF backing rod. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2600 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2609 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 25 | - | - | FMEMA | - | -/180/60 | 180 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the top face of the floor, backed by two 25 mm PEF backing rods. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2601 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2610 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 30 | - | - | FMEMA | - | -/180/120 | 180 minute | Linear gap seal up to 60 mm wide, with 30 mm deep sealant applied flush with the top face of the floor, backed by three 20 mm PEF backing rods. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2602 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2611 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 6 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 60 mm wide, with 6 mm deep sealant applied flush with the top face of the floor, backed by stone wool insulation to a minimum depth of 50 mm. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2603 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2612 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 6 | - | - | FMEMA | - | -/90/60 | 90 minute | Linear gap seal up to 60 mm wide, with 6 mm deep sealant applied flush with the underside of the floor, backed by stone wool insulation to a minimum depth of 50 mm. System installed to one side only of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2604 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2613 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 12 | 6 | - | - | FMEMA | - | -/240/120 | 240 minute | Linear gap seal up to 12 mm wide, with 6 mm deep sealant applied flush with the top face of the floor, backed by a 13 mm PEF backing rod. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2605 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2614 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 30 | 15 | - | - | FMEMA | - | -/240/180 | 240 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with the top face of the floor, backed by a 30 mm PEF backing rod. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2606 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2615 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 25 | - | - | FMEMA | - | -/240/60 | 240 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with the top face of the floor, backed by two 25 mm PEF backing rods. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2607 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2616 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 30 | - | - | FMEMA | - | -/240/120 | 240 minute | Linear gap seal up to 60 mm wide, with 30 mm deep sealant applied flush with the top face of the floor, backed by three 20 mm PEF backing rods. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2608 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2617 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 6 | - | - | FMEMA | - | -/240/180 | 240 minute | Linear gap seal up to 60 mm wide, with 6 mm deep sealant applied flush with the top face of the floor, backed by stone wool insulation to a minimum depth of 50 mm. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2609 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2618 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 6 | - | - | FMEMA | - | -/90/60 | 90 minute | Linear gap seal up to 60 mm wide, with 6 mm deep sealant applied flush with the underside of the floor, backed by stone wool insulation to a minimum depth of 50 mm. System installed to one side only of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2610 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2619 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 150 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 12 | 6 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 12 mm wide, with 6 mm deep sealant applied flush with both sides of the wall, backed by a 13 mm PEF backing rod. System installed both sides of a 150 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2611 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2620 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 150 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 30 | 15 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with both sides of the wall, backed by a 30 mm PEF backing rod. System installed both sides of a 150 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2612 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2621 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 150 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 25 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with both sides of the wall, backed by three 13 mm PEF backing rods. System installed both sides of a 150 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2613 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2622 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 150 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 5 | - | - | FMEMA | - | -/180/180 | 180 minute | Linear gap seal up to 60 mm wide, with 5 mm deep sealant applied flush with both sides of the wall, backed by stone wool insulation to a minimum depth of 50 mm. System installed both sides of a 150 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2614 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2623 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 175 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 12 | 6 | - | - | FMEMA | - | -/300/300 | 300 minute | Linear gap seal up to 12 mm wide, with 6 mm deep sealant applied flush with both sides of the wall, backed by a 13 mm PEF backing rod. System installed both sides of a 175 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2615 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2624 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 175 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 30 | 15 | - | - | FMEMA | - | -/300/300 | 300 minute | Linear gap seal up to 30 mm wide, with 15 mm deep sealant applied flush with both sides of the wall, backed by a 30 mm PEF backing rod. System installed both sides of a 175 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2616 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2625 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 175 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 25 | - | - | FMEMA | - | -/240/180 | 240 minute | Linear gap seal up to 50 mm wide, with 25 mm deep sealant applied flush with both sides of the wall, backed by three 13 mm PEF backing rods. System installed both sides of a 175 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2617 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2626 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 175 mm thick AAC wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 60 | 5 | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 60 mm wide, with 5 mm deep sealant applied flush with both sides of the wall, backed by stone wool insulation to a minimum depth of 50 mm. System installed both sides of a 175 mm thick wall system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2618 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2627 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 25 | 10 top side 10 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 25 mm wide, with 10 mm deep sealant applied flush with both faces of the floor, backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2619 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2628 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 10 top side 15 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 50 mm wide, with sealant applied 10 mm deep to the topside of the floor and 15 mm deep to the underside of the floor. The sealant was backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2620 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2629 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 100 | 10 top side 15 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 100 mm wide, with sealant applied 10 mm deep to the topside of the floor and 15 mm deep to the underside of the floor. The sealant was backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2621 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2630 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 150 | 10 | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 150 mm wide, with 10 mm deep sealant applied flush with the top face of the floor, backed by 1 layer of 25 mm thick Rockwool 825 FireBatt. 1 layer of 25 mm thick Rockwool 825 FireBatt was also applied flush to the underside of the the floor. System installed in 150 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2622 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2631 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 25 | 10 top side 10 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 25 mm wide, with 10 mm deep sealant applied flush with both faces of the floor, backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2623 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2632 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 50 | 10 top side 15 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 50 mm wide, with sealant applied 10 mm deep to the topside of the floor and 15 mm deep to the underside of the floor. The sealant was backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2624 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2633 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 100 | 10 top side 15 underside | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 100 mm wide, with sealant applied 10 mm deep to the topside of the floor and 15 mm deep to the underside of the floor. The sealant was backed by 2 layers of 12.5 mm thick ceramic fiber wool (Kaowool) to the underside face and 15 mm polyethylene foam to the top side face. System installed to both sides of a 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2625 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2634 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 175 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | - | 150 | 10 | - | - | FMEMA | - | -/240/240 | 240 minute | Linear gap seal up to 150 mm wide, with 10 mm deep sealant applied flush with the top face of the floor, backed by 1 layer of 25 mm thick Rockwool 825 FireBatt. 1 layer of 25 mm thick Rockwool 825 FireBatt was also applied flush to the underside of the the floor. System installed in 175 mm thick floor system. | FAS190037 R2.0 | - | 2024-12-16 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2626 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2635 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up with an approved material to achieve a 100mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 m maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2627 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2636 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/45 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2628 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2637 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up with an approved material to achieve a 100mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2629 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2638 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC50 | -/60/45 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2630 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2639 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2631 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2640 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2632 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2641 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up with an approved material to achieve a 100mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2633 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2642 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC100 | -/60/45 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2634 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2643 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up with an approved material to achieve a 100mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC DWV pipe with 5.0 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2635 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2644 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC150 | -/60/45 | 60 minute | Up to 150 mm uPVC DWV pipe with 5.0 mm maximum wall thickness. Sealant 5 mm deep in 7.5 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2636 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2645 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 4 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness. Sealant 5 mm deep in 4.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2637 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2646 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 2 | - | 5 | - | - | MC, FM300 | MC125 | -/30/30 | <60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness. Sealant 5 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2638 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2647 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 - 160 | 125 | 160 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 4 | - | 5 | - | - | MC, FM300 | Size to fit | -/45/45 | <60 minute | 125 mm - 160 mm HDPE pipe with 7.5 mm maximum wall thickness. Sealant 5 mm deep in 4.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2639 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2648 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 160 | 40 | 160 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC150 | -/60/60 | 60 minute | 40 mm - 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2640 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2649 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC32 | -/60/45 | 60 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2641 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2650 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 - 125 | 32 | 125 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | As required | Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/60/60 | 60 minute | 32 mm - 125 mm PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. Wall to be built up as appropriate with an approved material to achieve a 100 mm thick wall. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2642 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2651 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 - 125 | 32 | 125 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/60/45 | 60 minute | 32 mm - 125 mm PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2643 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2652 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC125 | -/60/45 | 60 minute | Up to 125 mm PPR pipe with 11.4 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2644 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2653 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC32 | -/60/45 | 60 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2645 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2654 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm PPR pipe with 2.9 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2646 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2655 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2647 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2656 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 - 125 | 32 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/60/60 | 60 minute | 32 mm - 125 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2648 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2657 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC125 | -/120/120 | 120 minute | Up to 125 mm PPR pipe with 3.1 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2649 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2658 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm PPR pipe with 4.0 mm - 14.6 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2650 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2659 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 1.8 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2651 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2660 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2652 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2661 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 - 7.4 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2653 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2662 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC pipe with 6.0 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2654 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2663 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 6.2 mm - 9.5 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2655 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2664 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2656 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2665 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm HDPE pipe with 2.9 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2657 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2666 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm HDPE pipe with 2.7 mm -10.0 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2658 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2667 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 120 | 40 | 120 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | Size to fit | -/60/45 | 60 minute | 40 mm - 120 mm HDPE pipe with 3.2 mm - 11.4 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2659 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2668 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 120 - 150 | 120 | 150 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | Size to fit | -/45/45 | <60 minute | 120 mm - 150 mm HDPE pipe with 11.4 mm - 14.5 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2660 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2669 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2661 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2670 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 160 | 40 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | Size to fit | -/60/60 | 60 minute | 40 mm - 160 mm HDPE pipe with 3.2 mm - 14.5 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2662 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2671 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2663 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2672 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2664 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2673 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2665 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2674 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2666 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2675 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2667 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2676 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2668 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2677 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 7.5 | - | 5 | - | - | MC, FM300 | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2669 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2678 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 20 | - | - | - | - | MC | MC200 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 2.8 mm maximum wall thickness. The service included 12 mm thick Armaflex lagging, with a 200 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2670 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2679 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2671 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2680 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2672 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2681 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2673 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2682 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2674 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2683 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2675 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2684 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2676 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2685 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | As required | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. Localised build-up is required to achieve the required rating. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2677 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2686 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC150 | -/60/45 | 60 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2678 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2687 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC150 | -/60/60 | 60 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2679 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2688 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3 - 4.5 | - | 13 | - | - | MC, FMHPE | MC32 | -/60/60 | 60 minute | Up to 32 mm PEX pipe with 3.2 mm maximum wall thickness. Sealant 13.0 mm deep in 3.0 mm - 4.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2680 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2689 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3 - 4.0 | - | 13 | - | - | MC, FMHPE | MC32 | -/60/45 | 60 minute | Up to 32 mm PEX-AL-PEX pipe with 3.0 mm maximum wall thickness. Sealant 13.0 mm deep in 3.0 mm - 4.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2681 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2690 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | 1-sided installation - Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 5.0 mm annular gap to penetrated sides. 40 mm BOSS MaxiCollar™ installed on the penetrated side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2682 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2691 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2683 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2692 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2684 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2693 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2685 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2694 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2686 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2695 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2687 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2696 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 10 | - | - | MC, FM300 | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2688 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2697 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2689 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2698 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 4 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness. Sealant 5.0 mm deep in 4.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2690 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2699 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 2 | - | 5 | - | - | MC, FM300 | MC125 | -/120/45 | 120 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness. Sealant 5.0 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2691 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2700 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 2.5 | - | 5 | - | - | MC, FM300 | MC160 | -/60/60 | 60 minute | Up to 160 mm HDPE pipe with 14.5 mm maximum wall thickness. Sealant 5.0 mm deep in 2.5 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2692 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2701 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 150 | 40 | 150 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 12.5 | - | - | MC, FM300 | Size to fit | -/60/60 | 60 minute | 40 mm - 150 mm HDPE pipe with 14.5 mm maximum wall thickness. Sealant 12.5 mm deep in 9.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2693 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2702 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 150 - 160 | 150 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 12.5 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | 150 mm - 160 mm HDPE pipe with 14.5 mm maximum wall thickness. Sealant 12.5 mm deep in 9.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2694 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2703 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1.5 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 1.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2695 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2704 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/90 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2696 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2705 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/90/90 | 90 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2697 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2706 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2698 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2707 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 - 125 | 110 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 2 | - | 5 | - | - | MC, FM300 | MC125 | -/30/30 | <60 minute | 110 mm - 125 mm PPR pipe with 11.4 mm maximum wall thickness. Sealant 5.0 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2699 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2708 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 - 160 | 125 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | Size to fit | -/90/90 | 90 minute | 125 mm - 160 mm PPR pipe with 11.4 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2700 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2709 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 9 | - | 5 | - | - | MC, FM300 | MC40 | -/90/90 | 90 minute | 1-sided installation - Up to 40 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 9.0 mm annular gap to penetrated sides. 40 mm BOSS MaxiCollar™ installed on the penetrated side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2701 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2710 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2702 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2711 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 160 | 160 | Wall | 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2703 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2712 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 250 | 250 | 250 | Wall | 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC250 | -/120/120 | 120 minute | Up to 250 mm PP/PPR pipe with 6.2 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 250 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2704 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2713 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Wall | 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2705 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2714 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 160 | 160 | 160 | Wall | 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2706 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2715 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 400 | 400 | 400 | Wall | 150 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | - | - | - | - | - | 0 | - | - | - | - | MC | MC400 | -/15/15 | <60 minute | 400 mm PE pipe with 8.0 mm maximum wall thickness. 400 mm BOSS MaxiCollar™ installed on both sides. Tested Capped/Uncapped. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2707 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2716 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | - | - | - | - | - | 11 | - | - | - | - | MC | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2708 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2717 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2709 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2718 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2710 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2719 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2711 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2720 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2712 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2721 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2713 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2722 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2714 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2723 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 3.5 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2715 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2724 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2716 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2725 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | - | - | - | MC, FM300 | MC40 | -/240/240 | 240 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2717 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2726 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/240/240 | 240 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2718 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2727 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2719 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2728 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/240/240 | 240 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2720 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2729 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/240/240 | 240 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2721 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2730 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC100 | -/240/240 | 240 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2722 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2731 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC150 | -/240/240 | 240 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2723 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2732 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 3.5 | - | 5 | - | - | MC, FM300 | MC40 | -/240/240 | 240 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2724 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2733 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC150 | -/240/240 | 240 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2725 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2734 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 320 mm x 320 mm BOSS Batt™ on the exposed side of the main 1200 mm x 500 mm BOSS Batt™ aperture protection - Installed in min 100 mm thick walls. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 5 | Up to 1200 x 500 | - | - | - | BB-50, AC, FM300, MC | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes an additional 320 mm x 320 mm section of Batt to the exposed side secured with pigtail screws at 50 mm in from the edges on four sides, with a 100 mm BOSS MaxiCollar™ installed to both sides. A 10 mm bead of sealant applied on the perimeter of the batt as a smoke seal. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2726 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2735 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 1 layer of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 76 mm thick walls. | 1 | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 76 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC110 | -/60/60 | 60 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The BOSS Batt™ was friction fitted within the aperture flush to the face. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. For framed systems, the BOSS Batt™ is to be centrally located within the wall with maximum 50 mm timber or steel framing. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2727 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2736 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 1 layer of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 76 mm thick walls. | 1 | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 76 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC110 | -/60/60 | 60 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The BOSS Batt™ was friction fitted within the aperture flush to the face. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. For framed systems, the BOSS Batt™ is to be centrally located within the wall with maximum 50 mm timber or steel framing. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2728 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2737 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 76 mm thick walls. | 1 | - | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 76 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC50 | -/60/60 | 60 minute | Up to 50 mm PPR pipe with 2.9 mm wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The BOSS Batt™ was friction fitted within the aperture flush to the face. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. For framed systems, the BOSS Batt™ is to be centrally located within the wall with maximum 50 mm timber or steel framing. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2729 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2738 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness, penetrating 2 layers of friction or pattress fitted BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2730 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2739 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness, penetrating 2 layers of friction or pattress fitted BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2731 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2740 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm PPR pipe with 2.9 mm wall thickness, penetrating 2 layers of friction or pattress fitted BOSS Batt™ protecting an aperture up to 600 mm x 600 mm sealed at the interface of the wall with sealant. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2732 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2741 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2733 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2742 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2734 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2743 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2735 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2744 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2736 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2745 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2737 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2746 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2738 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2747 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2739 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2748 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2740 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2749 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2741 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2750 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 100 | 40 | 100 | Wall | 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | Size to fit | -/60/60 | 60 minute | 40 mm - 100 mm HDPE pipe with 2.9 mm - 11.4 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2742 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2751 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2743 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2752 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2744 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2753 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2745 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2754 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2746 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2755 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2747 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2756 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC100 | -/90/90 | 90 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2748 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2757 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | BOSS Batt™ | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. BOSS Batt™ pattress installed to exposed side of the system. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2749 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2758 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2750 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2759 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed to the exposed side only. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2751 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2760 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed to the exposed side only. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2752 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2761 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | Fill area around pipe | Up to 1200 x 500 | 10 | NA | - | BB-50, AC, FM300, MC | MC110 | -/90/90 | 120 minute | Up to 50 mm PP / PP-R pipe with 2.9 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The pipe was installed at a 30° angle to the separating element through a 50 mm x 96 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2753 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2762 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | Fill area around pipe | Up to 1200 x 500 | 10 | NA | - | BB-50, AC, FM300, MC | MC160 | -/120/90 | 120 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The pipe was installed at a 30° angle to the separating element through a 156 mm x 110 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2754 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2763 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | Fill area around pipe | Up to 1200 x 500 | 10 | NA | - | BB-50, AC, FM300, MC | MC160 | -/90/90 | 120 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The pipe was installed at a 30° angle to the separating element through a 156 mm x 110 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2755 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2764 | Plastic_Pipes | Concentric 60/100 plastic pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 60/100 | 60/100 | 60/100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC110 | -/120/120 | 120 minute | Concentric 60/100 plastic pipe - 101 mm outer pipe with 1.9 mm wall thickness, and 60 mm inner pipe with 2.0 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 110 mm BOSS MaxiCollar™ installed to the unexposed side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2756 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2765 | Plastic_Pipes | Concentric c80/120 plastic pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 80/120 | 80/120 | 80/120 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC125 | -/120/120 | 120 minute | Concentric 80/120 plastic pipe - 121 mm outer pipe with 1.5 mm wall thickness, and 82 mm inner pipe with 2.4 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 125 mm BOSS MaxiCollar™ installed to the unexposed side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2757 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2766 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 33 | 0 | 33 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0.8 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC40 | -/120/120 | 120 minute | Up to 33.4 mm cPVC pipe with 2.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2758 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2767 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0.9 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC40 | -/120/90 | 120 minute | Up to 42.2 mm cPVC pipe with 3.3 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2759 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2768 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 48 | 0 | 48 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0.85 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC50 | -/120/120 | 120 minute | Up to 48.3 mm cPVC pipe with 3.8 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2760 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2769 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0.85 | Up to 1200 x 500 | NA | NA | - | BB-50, AC, MC | MC65 | -/120/90 | 120 minute | Up to 60.3 mm cPVC pipe with 4.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The system includes a 65 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2761 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2770 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 6 | Up to 1200 x 500 | Depth of collar | NA | - | BB-50, AC, FMHPE, MC | MC32 | -/60/60 | 60 minute | Up to 20 mm PP / PP-R pipe with 4.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2762 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2771 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 10 | Up to 1200 x 500 | Depth of collar | NA | - | BB-50, AC, FMHPE, MC | MC32 | -/60/30 | 60 minute | Up to 20 mm PEX pipe with 6.3 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2763 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2772 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 2.5 | Up to 1200 x 500 | Depth of collar | NA | - | BB-50, AC, FMHPE, MC | MC40 | -/60/30 | 60 minute | Up to 25 mm PEX pipe with 6.2 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2764 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2773 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides. | 1 | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 2.5 | Up to 1200 x 500 | Depth of collar | NA | - | BB-50, AC, FMHPE, MC | MC32 | -/60/30 | 60 minute | Up to 25 mm PEX-AL pipe with 5.3 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2765 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2774 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 144 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | 1 | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | 3.5 | Up to 1200 x 500 | Depth of collar | NA | - | BB-50, AC, FMHPE, MC | MC32 | -/120/60 | 120 minute | Up to 25 mm PEX pipe with 3.1 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2766 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2775 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 78 mm thick walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 2.5 | Up to 1200 x 500 | 10 | 5 | - | BB-50, AC, FM300, FMHPE, MC | MC150 | -/240/60 | 240 minute | Up to 110 mm uPVC DWV pipe with 3.5 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. FM-300 sealant installed around service 10 mm deep in annular gap finished flush both sides. FM-HPE sealant was also applied as a 5 mm fillet on the joint between the collar and panel both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2767 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2776 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 78 mm thick walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 2.5 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC150 | -/120/90 | 120 minute | Up to 110 mm uPVC DWV pipe with 3.5 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. FM-300 sealant applied on the joint between the collar and panel both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2768 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2777 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 78 mm thick walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 6 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC205 | -/240/120 | 240 minute | Up to 160 mm cPVC pipe with 7.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. FM-300 sealant applied on the joint between the collar and panel both sides. The system includes a 205 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2769 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2778 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 13.5 | - | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC DWV pipe. When installed in ComFlor® 60 (Composite floor deck), a 330 mm x 330 mm section of BOSS Batt is to be installed to the underside of the floor system, with the gap between the BOSS Batt and the top rib filled with a trapezoid shape section of BOSS Batt. Sealant to depth of 5 mm between the pipe and the aperture finished flush on both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2770 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2779 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 75 | 0 | 75 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 8.5 | - | 5 | - | - | BB-50, AC, FM300, MC | MC75 | -/120/120 | 120 minute | Up to 75 mm HDPE pipe. When installed in ComFlor® 60 (Composite floor deck), a 290 mm x 290 mm section of BOSS Batt is to be installed to the underside of the floor system, with the gap between the BOSS Batt and the top rib filled with a trapezoid shape section of BOSS Batt. Sealant to depth of 5 mm between the pipe and the aperture finished with a 10 mm x 10 mm fillet on the top side and finished at 5 mm depth flush on the underside. The system includes a 75 mm BOSS MaxiCollar™ installed to the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2771 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2780 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2772 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2781 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2773 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2782 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2774 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2783 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2775 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2784 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2776 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2785 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2777 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2786 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 125 mm uPVC pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2778 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2787 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 3.5 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2779 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2788 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2780 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2789 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 3.5 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm PP/PPR pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 1.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2781 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2790 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2782 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2791 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC55 | -/90/90 | 90 minute | Up to 50 mm PP/PPR pipe with 1.8 mm - 6.9 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2783 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2792 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC55 | -/120/120 | 120 minute | Up to 50 mm PP/PPR pipe with 6.9 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2784 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2793 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC110 | -/60/60 | 60 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2785 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2794 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC110 | -/15/15 | <60 minute | Up to 110 mm PP/PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2786 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2795 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm PP/PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2787 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2796 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm PP/PPR pipe with 3.1 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2788 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2797 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm PP/PPR pipe with 4.0 mm - 14.6 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2789 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2798 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC55 | -/60/60 | 60 minute | Up to 50 mm PE pipe with 3.0 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2790 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2799 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC55 | -/45/45 | <60 minute | Up to 50 mm PE pipe with 3.0 mm - 4.6 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2791 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2800 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm PE pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2792 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2801 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC110 | -/30/30 | <60 minute | Up to 110 mm PE pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2793 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2802 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC110 | -/15/15 | <60 minute | Up to 110 mm PE pipe with 2.7 mm - 10.0 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2794 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2803 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm PE pipe with 3.1 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2795 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2804 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2796 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2805 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2797 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2806 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 1.8 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2798 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2807 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC55 | -/90/60 | 90 minute | Up to 50 mm uPVC pipe with 2.4 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2799 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2808 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2800 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2809 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2801 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2810 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm uPVC pipe with 4.2 mm - 7.3 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2802 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2811 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 10 | - | - | MC, FM300 | MC110 | -/30/30 | <60 minute | Up to 110 mm uPVC pipe with 4.2 mm - 6.6 mm maximum wall thickness. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2803 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2812 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm uPVC pipe with 6.0 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2804 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2813 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.0 mm maximum wall thickness. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2805 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2814 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm uPVC pipe with 6.2 mm - 9.5 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2806 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2815 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm HDPE pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2807 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2816 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm HDPE pipe with 10.0 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2808 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2817 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 5 | - | - | MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2809 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2818 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2810 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2819 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2811 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2820 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, installed with 2 90° fittings on the underside to form a U-bend that penetrates the separating element twice. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides for each penetration point. 110 mm BOSS MaxiCollar™ installed on both sides of each penetration point. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2812 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2821 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/120/- | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness, installed with 2 90° fittings on the underside to form a U-bend that penetrates the separating element twice. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides for each penetration point. 160 mm BOSS MaxiCollar™ installed on both sides of each penetration point. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2813 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2822 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 19 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.3 mm maximum wall thickness. Sealant used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2814 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2823 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 19 | - | - | MC, FM300 | MC40 | -/90/90 - RISF 48 min | 90 minute | Up to 32 mm uPVC DWV pipe with 2.3 mm maximum wall thickness. Sealant used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. 40 mm BOSS MaxiCollar™ installed on the underside. The specimen also achieved RSIF of 55 minutes. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2815 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2824 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2816 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2825 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2817 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2826 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2818 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2827 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2819 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2828 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC80 | -/60/60 | 60 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2820 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2829 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC80 | -/90/90 - RISF 53 min | 90 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 80 mm BOSS MaxiCollar™ installed on the underside. The specimen also achieved RSIF of 53 minutes. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2821 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2830 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC65 | -/60/60 | 60 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 65 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2822 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2831 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC65 | -/90/90 - RISF 24 min | 90 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 65 mm BOSS MaxiCollar™ installed on the underside. The specimen also achieved RSIF of 24 minutes. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2823 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2832 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 19 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.3 mm maximum wall thickness. Sealant used to seal the particle board flooring to its full depth in the annular gap on the top side, finished flush. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2824 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2833 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2825 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2834 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2826 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2835 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2827 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2836 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 6.0 mm annular gap both sides, finished flush. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2828 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2837 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC80 | -/60/60 | 60 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2829 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2838 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | Top 23.5 Bottom 13.0 | - | Top 19 and bottom depth of collar | - | - | MC, FM300, FMHPE | MC65 | -/60/60 | 60 minute | Up to 25 mm uPVC conduit with 2.0 mm maximum wall thickness. FM-300 sealant used to seal the 19 mm particle board flooring to its full depth in the 23.5 mm annular gap on the top side, finished flush. FM-HPE to fill the 13.0 mm annular gap between the fire collar and pipe to its full depth on the underside. 65 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2830 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2839 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | Boss FireMortar-360™ | - | - | - | - | - | 1400 x 700 | - | - | - | MC, FM360 | MC110 | -/120/120 | 120 minute | Up to 110 mm PE pipe with 4.2 mm maximum wall thickness, penetrating a 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360 gypsum based mortar, flush with the top face of the floor. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2831 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2840 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | Boss FireMortar-360™ | - | - | - | - | - | 1400 x 700 | - | - | - | MC, FM360 | MC160 | -/120/120 | 120 minute | Up to 160 mm PE pipe with 9.5 mm maximum wall thickness, penetrating a 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360 gypsum based mortar, flush with the top face of the floor. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2832 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2841 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS MaxiCollar™ | Boss FireMortar-360™ | - | - | - | - | - | 1400 x 700 | - | - | - | MC, FM360 | MC160 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 9.5 mm maximum wall thickness, penetrating a 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360 gypsum based mortar, flush with the top face of the floor. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2833 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2842 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2834 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2843 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2835 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2844 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2836 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2845 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2837 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2846 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2838 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2847 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2839 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2848 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2840 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2849 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 2.9 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2841 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2850 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 125 | 40 | 125 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 12.5 | - | 5 | - | - | MC, FM300 | Size to fit | -/30/30 | <60 minute | 40 mm to 125 mm HDPE pipe with 3.2 mm - 11.4 mm maximum wall thickness. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. BOSS MaxiCollar™ to suit pipe size, installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2842 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2851 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2843 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2852 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2844 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2853 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2845 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2854 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2846 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2855 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2847 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2856 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC100 | -/90/90 | 90 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2848 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2857 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2849 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2858 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 2.9 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2850 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2859 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 12.5 | - | 5 | - | - | MC, FM300, FMHPE | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.5 mm maximum wall thickness. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2851 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2860 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 5 | - | 5 | 10 | - | BB-50, AC, FM300, MC | MC32 | -/120/120 | 120 minute | Up to 25 mm uPVC pipe with 2.2 mm maximum wall thickness. When installed in ComFlor® 60 (Composite floor deck), a 265 mm x 265 mm section of BOSS Batt is to be installed to the underside of the floor system, with the gap between the BOSS Batt and the top rib filled with a trapezoid shape section of BOSS Batt. Sealant to depth of 5 mm on both sides, finished with a 10 mm x 10 mm fillet on the top side. 32 mm BOSS MaxiCollar™ installed to the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2852 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2861 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in 1000 mm x 350 mm aperture in min 150mm thick AAC floors. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 1000 x 350 | - | - | - | BB-50, AC, FM300, MC | MC140 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with maximum wall thickness of 4.2mm. Two layers of 50 mm thick BOSS Batt fitted back-to-back and bedded within a 1000 mm x 350 mm wide aperture using BOSS FireMastic-300™ sealant. The overall size was made of cut batt sections butt jointed together with sealant. 140 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2853 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2862 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in 1000 mm x 350 mm aperture in min 150mm thick AAC floors. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 1000 x 350 | - | - | - | BB-50, AC, FM300, MC | MC200 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with maximum wall thickness of 9.5mm. Two layers of 50 mm thick BOSS Batt fitted back-to-back and bedded within a 1000 mm x 350 mm wide aperture using BOSS FireMastic-300™ sealant. The overall size was made of cut batt sections butt jointed together with sealant. 200 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  | Tested Uncapped/Capped | BF-2854 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2863 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in 1000 mm x 350 mm aperture in min 150mm thick AAC floors. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 0 | Up to 1000 x 350 | - | - | - | BB-50, AC, FM300, MC | MC200 | -/120/120 | 120 minute | Up to 160 mm PE pipe with maximum wall thickness of 9.5mm. Two layers of 50 mm thick BOSS Batt fitted back-to-back and bedded within a 1000 mm x 350 mm wide aperture using BOSS FireMastic-300™ sealant. The overall size was made of cut batt sections butt jointed together with sealant. 200 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  | Tested Uncapped/Capped | BF-2855 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2864 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 78 mm Speedpanel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS OneWay collar | BOSS FireMastic-300™ | - | - | - | - | 15 | 130 | Full depth | - | - | OWC, FM300 | OWC100 | -/120/90 | 120 minute | 100 mm uPVC pipe with 3.3 mm maximum wall thickness, installed through a 100 mm BOSS OneWay collar centrally located through the separating element. Sealant installed full depth in 15.0 mm annular gap between the aperture and the in-wall collar. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2856 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2865 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS OneWay collar | BOSS FireMastic-300™ | - | - | - | - | 27.5 | 155 | 25 | - | - | OWC, FM300 | OWC100 | -/120/120 | 120 minute | 100 mm uPVC pipe with 3.3 mm maximum wall thickness, installed through a 100 mm BOSS OneWay collar, installed flush with the top of the floor. Sealant installed 25 mm deep in the annular gap between the separating element, the service and the metal sleeve to the top side. Sealant was also installed 5 mm deep in the annular gap between the separating element, the service and the metal sleeve to the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2857 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2866 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 218 x 74 | 218 x 74 | 218 x 74 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | - | 218 x 74 | Surface | - | - | UW-25, FM300, PWP | 3 layers of UW-25 | -/120/120 | 120 minute | 204 mm x 60 mm uPVC duct with 2.5 mm maximum wall thickness. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2858 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2867 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 x 54 | 110 x 54 | 110 x 54 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | - | 126 x 62 | Surface | - | - | UW-25, FM300, PWP | 3 layers of UW-25 | -/15/15 | <60 minute | 110 mm x 54 mm uPVC duct with 2.0 mm maximum wall thickness. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2859 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2868 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 220 x 90 | 220 x 90 | 220 x 90 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | - | 236 x 98 | Surface | - | - | UW-25, FM300, PWP | 3 layers of UW-25 | -/60/60 | 60 minute | 220 mm x 90 mm uPVC duct with 2.0 mm maximum wall thickness. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2860 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2869 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 35 | - | - | 25 (Wall) x 40 (Pipe) | - | UW-25, FM300, PWP | 5 layers of UW-25 | -/120/120 | 120 minute | 200 mm uPVC pipe with 7.7 mm maximum wall thickness. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Fillet of sealant applied 25 mm wide (wall) x 40 mm deep (pipe) on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  | Tested Uncapped/Capped | BF-2861 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2870 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 10 | - | 26 | - | - | UW-25, FM300, PWP | 1 layer of UW-25 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.7 mm maximum wall thickness. 1 layer of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 10.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2862 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2871 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 10 | - | 26 | - | - | UW-25, FM300, PWP | 2 layers of UW-25 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 3.5 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 10.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2863 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2872 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 11 | - | 26 | - | - | UW-25, FM300, PWP | 2 layers of UW-25 | -/120/- | 120 minute | Up to 80 mm uPVC pipe with 3.4 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 11.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2864 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2873 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 33.4 | 0 | 33.4 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 5 | - | - | 5 | - | UW-25, FM300, PWP | 2 layers of UW-25 | -/120/60 | 120 minute | Up to 33.4 mm cPVC pipe with 2.6 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2865 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2874 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 48.3 | 0 | 48.3 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 4.85 | - | - | 5 | - | UW-25, FM300, PWP | 2 layers of UW-25 | -/120/90 | 120 minute | Up to 48.3 mm cPVC pipe with 3.8 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2866 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2875 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60.3 | 0 | 60.3 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 4.85 | - | - | 5 | - | UW-25, FM300, PWP | 2 layers of UW-25 | -/120/90 | 120 minute | Up to 60.3 mm cPVC pipe with 4.7 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2867 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2876 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | - | - | - | - | 5 | - | - | - | - | UW-25, PWP | 2 layers of UW-25 | -/60/60 | 60 minute | Up to 25 mm PEX pipe with 6.2 mm maximum wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-2868 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2877 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 31 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 3 layers of UW-25 | -/120/90 | 120 minute | Up to 40 mm uPVC pipe with 1.9 mm wall thickness, insulated with 25 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 31.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2869 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2878 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 21 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 3 layers of UW-25 | -/120/90 | 120 minute | Up to 40 mm uPVC pipe with 3.0 mm wall thickness, insulated with 15 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 21.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2870 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2879 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 38 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 3 layers of UW-25 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 1.9 mm wall thickness, insulated with 32 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 38.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2871 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2880 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 15 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 3 layers of UW-25 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 3.0 mm wall thickness, insulated with 9 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 15.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2872 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2881 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 35 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 5 layers of UW-25 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 mm wall thickness, insulated with 25 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that also included a 100 mm insulation cut back from the opening. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 35.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2873 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2882 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 30 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 5 layers of UW-25 | -/120/90 | 120 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness, insulated with 20 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 30.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2874 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2883 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 42 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 5 layers of UW-25 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 mm wall thickness, insulated with 32 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 42.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2875 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2884 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 23 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25, PWP | 5 layers of UW-25 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness, insulated with 13 mm thick phenolic foam. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 600 mm x 600 mm, that overlapped the aperture by 100 mm on all sides. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 23.0 mm annular gap. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2876 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2885 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | 10 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, FMHPE, UW-25, PWP | 4 layers of UW-25 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 7.6 mm wall thickness. The system penetrated 2 layers of BOSS Batt™ friction fitted and bedded in a 600 mm x 600 mm aperture. All edges sealed with BOSS FireMastic-300™ sealant. 4 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 10.0 mm annular gap. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides with BOSS FireMastic-HPE™. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2877 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2886 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 470mm x 470mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 10 | Up to 470 x 470 | - | - | - | BB-50, AC, FM300, UW-25, PWP | 4 layers of UW-25 | -/60/60 | 60 minute | Up to 110 mm uPVC pipe with 4.9mm wall thickness. The system penetrated 2 layers of BOSS Batt™, with each layer patressed on either side protecting an aperture up to 470 mm x 470 mm, that overlapped the aperture by 100 mm on all sides. All edges sealed with BOSS FireMastic-300™ sealant. 4 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 10.0 mm annular gap. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides with BOSS FireMastic-HPE™. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2878 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2887 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | 6 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, FMHPE, UW-25, PWP | 4 layers of UW-25 | -/90/90 | 90 minute | Up to 110 mm uPVC pipe with 5.2 mm wall thickness. The system penetrated 2 layers of BOSS Batt™ friction fitted and bedded in a 600 mm x 600 mm aperture. All edges sealed with BOSS FireMastic-300™ sealant. 4 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 6.0 mm annular gap. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides with BOSS FireMastic-HPE™. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2879 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2888 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 120 | 0 | 120 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | 6 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, FMHPE, UW-25, PWP | 4 layers of UW-25 | -/90/90 | 90 minute | Up to 120 mm PP/PPR pipe with 3.6 mm wall thickness. The system penetrated 2 layers of BOSS Batt™ friction fitted and bedded in a 600 mm x 600 mm aperture. All edges sealed with BOSS FireMastic-300™ sealant. 4 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 6.0 mm annular gap. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides with BOSS FireMastic-HPE™. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2880 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2889 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 126 | 0 | 126 | Wall | 2 layers of 50 mm BOSS Batt™ installed in 600mm x 600mm aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides. | - | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | 6 | Up to 600 x 600 | - | - | - | BB-50, AC, FM300, FMHPE, UW-25, PWP | 4 layers of UW-25 | -/90/90 | 90 minute | Up to 110 mm PE pipe with 3.4 mm wall thickness. The system penetrated 2 layers of BOSS Batt™ friction fitted and bedded in a 600 mm x 600 mm aperture. All edges sealed with BOSS FireMastic-300™ sealant. 4 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides installed in the 6.0 mm annular gap. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides with BOSS FireMastic-HPE™. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2881 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2890 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 6 | - | 10 | - | - | FM300, UW-25, PWP | 2 layers of UW-25 | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 2.0 mm - 6.9 mm wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2882 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2891 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 12 | - | 10 | - | - | FM300, UW-25, PWP | 10 layers of UW-25 | -/240/240 | 240 minute | Up to 200 mm PP/PPR pipe with 4.9 mm wall thickness. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2883 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2892 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 12 | - | 10 | - | - | FM300, UW-25, PWP | 10 layers of UW-25 | -/120/120 | 120 minute | Up to 200 mm PP/PPR pipe with 4.9 mm - 18.2 mm wall thickness. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2884 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2893 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 6 | - | 10 | - | - | FM300, UW-25, PWP | 2 layers of UW-25 | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 3.0 - 4.6 mm wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2885 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2894 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 12 | - | 10 | - | - | FM300, UW-25, PWP | 10 layers of UW-25 | -/240/240 | 240 minute | Up to 200 mm PP/PPR pipe with 4.9 mm - 18.2 mm wall thickness. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2886 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2895 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 6 | - | 10 | - | - | FM300, UW-25, PWP | 2 layers of UW-25 | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 2.4 mm - 3.7 mm wall thickness. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2887 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2896 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 12 | - | 10 | - | - | FM300, UW-25, PWP | 10 layers of UW-25 | -/60/60 | 60 minute | Up to 200 mm uPVC pipe with 7.7 mm - 9.6 mm wall thickness. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2888 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2897 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | - | 12 | - | 10 | - | - | FM300, UW-25, PWP | 10 layers of UW-25 | -/240/120 | 240 minute | Up to 200 mm uPVC pipe with 9.6 mm wall thickness. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2889 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2898 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS UniWrap™ | BOSS PWP Pipe Wrap | Boss FireMortar-360™ | - | - | - | 0 | Up to 1400 x 700 | - | - | - | UW-25, FM360, PWP | 10 layers of UW-25 | -/90/90 | 90 minute | Up to 200 mm uPVC pipe with 7.7 mm - 9.6 mm maximum wall thickness, penetrating a 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360 gypsum based mortar, flush with the top face of the floor. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap cast into the BOSS FireMortar-360 mid-depth of the floor. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2890 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2932 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm PE pipe with 3.0 - 4.6 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2891 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2933 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 110 mm PE pipe with 10.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2892 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2934 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/120/60 | 120 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2893 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2935 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 110 mm PE pipe with 2.7 - 10.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2894 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2936 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/120/120 | 120 minute | Up to 125 mm PE pipe with 3.1 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2895 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2937 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/90/90 | 90 minute | Up to 125 mm PE pipe with 3.1 - 11.4 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2896 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2938 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 160 mm PE pipe with 4.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2897 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2939 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 12.5 | - | - | MC, FM300 | MC125 | -/120/120 | 120 minute | Up to 125 mm PE pipe with 3.1 mm wall thickness. Sealant installed around service 12.5 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2898 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2940 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC50 | -/120/90 | 120 minute | Up to 50 mm PP/PPR pipe with 2.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2899 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2941 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC50 | -/120/60 | 120 minute | Up to 50 mm PP/PPR pipe with 2.0 - 6.9 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2900 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2942 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/120/90 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2901 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2943 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/90/90 | 90 minute | Up to 110 mm PP/PPR pipe with 2.7 - 10.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2902 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2944 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/120/90 | 120 minute | Up to 125 mm PP/PPR pipe with 3.1 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2903 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2945 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm PP/PPR pipe with 3.1 - 17.1 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2904 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2946 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/90/90 | 90 minute | Up to 160 mm PP/PPR pipe with 4.0 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2905 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2947 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/15/15 | <60 minute | Up to 160 mm PP/PPR pipe with 4.0 - 9.1 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2906 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2948 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC160 | -/15/15 | <60 minute | Up to 160 mm PP/PPR pipe with 9.1 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2907 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2949 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC50 | -/120/90 | 120 minute | Up to 50 mm uPVC pipe with 1.8 - 3.7 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2908 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2950 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC100 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 - 6.6 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2909 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2951 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/120/90 | 120 minute | Up to 125 mm uPVC pipe with 7.4 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2910 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2952 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC125 | -/90/90 | 90 minute | Up to 125 mm uPVC pipe with 4.8 - 7.4 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 125 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2911 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2953 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10 | - | 10 | - | - | MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 6.2 - 9.5 mm wall thickness. Sealant installed around service 10 mm deep in 10 mm annular gap finished flush both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2912 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2954 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 20 | - | - | - | - | MC | MC150 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 2.8 mm wall thickness. The service included 12 mm thick Armaflex lagging, with a 150 mm BOSS MaxiCollar™ installed to both sides. Installed in min 100 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2913 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2955 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3 | - | Depth of collar | - | - | MC, FMHPE | MC32 | -/60/60 | 60 minute | Up to 32 mm PP/PPR pipe with 5.8 mm wall thickness. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 3 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2914 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2956 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 5 | - | Depth of collar | - | - | MC, FMHPE | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 5.0 mm wall thickness. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2915 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2957 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 5 | - | Depth of collar | - | - | MC, FMHPE | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 4.5 mm wall thickness. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2916 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2958 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 5 | - | Depth of collar | - | - | MC, FMHPE | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 6.4 mm wall thickness. The system includes a 80 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2917 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2959 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 5 | - | Depth of collar | - | - | MC, FMHPE | MC50 | -/60/30 | 60 minute | Up to 50 mm cPVC pipe with 10.1 mm wall thickness. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. Sealant installed in the gap between the collar and pipe to full depth. Maximum 5 mm annular gap through substrate. Installed in min 118 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2918 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2960 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 5 | - | 10 | - | - | MC | MC100 | -/120/120 | 120 minute | 100 mm uPVC pipe with 3.2 mm wall thickness. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. Installed in min 144 mm thick walls. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2919 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2961 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 15 | - | 5 | - | - | MC, FM300 | MC40 | -/120/90 | 120 minute | Up to 40 mm uPVC pipe with 3.0 mm wall thickness. Sealant installed around service 5 mm deep in 15 mm annular gap finished flush both sides. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2920 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2962 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 13 | - | 5 | - | - | MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.6 mm wall thickness. Sealant installed around service 5 mm deep in 13 mm annular gap finished flush both sides. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2921 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2963 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 11 | - | 5 | - | - | MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 3.4 mm wall thickness. Sealant installed around service 5 mm deep in 11 mm annular gap finished flush both sides. The system includes a 80 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2922 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2964 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 10.5 | - | 5 | - | - | MC, FM300 | MC100 | -/120/- | 120 minute | Up to 100 mm uPVC pipe with 3.8 mm wall thickness. Sealant installed around service 5 mm deep in 10.5 mm annular gap finished flush both sides. The system includes a 100 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2923 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2965 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 m maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2924 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2967 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2925 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2969 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2926 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2970 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2927 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2971 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2928 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2973 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC DWV pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 7.5 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2929 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2975 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 4 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 4.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2930 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2976 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 2 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/30/30 | <60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2931 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2977 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 - 160 | 125 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 4 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/45/45 | <60 minute | 125 mm - 160 mm HDPE pipe with 7.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5 mm deep in 4.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2932 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2978 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 160 | 40 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/60 | 60 minute | 40 mm - 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2933 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2979 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC32 | -/60/45 | 60 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2934 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2980 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 - 125 | 32 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/60/60 | 60 minute | 32 mm - 125 mm PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2935 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2982 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 90 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/60/45 | 60 minute | Up to 125 mm PPR pipe with 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2936 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2983 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC32 | -/60/45 | 60 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2937 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2984 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm PPR pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2938 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2985 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2939 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2986 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 - 125 | 32 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC125 | -/60/60 | 60 minute | 32 mm - 125 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2940 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2987 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC125 | -/120/120 | 120 minute | Up to 125 mm PPR pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2941 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2988 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | Up to 160 mm PPR pipe with 4.0 mm - 14.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2942 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2989 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 1.8 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2943 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2990 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2944 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2991 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm uPVC pipe with 4.2 - 7.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2945 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2992 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC pipe with 6.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2946 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2993 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 6.2 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2947 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2994 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2948 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2995 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm HDPE pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2949 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2996 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm HDPE pipe with 2.7 mm -10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2950 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2997 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 120 | 40 | 120 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/60/45 | 60 minute | 40 mm - 120 mm HDPE pipe with 3.2 mm - 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2951 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2998 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 120 - 150 | 120 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/45/45 | <60 minute | 120 mm - 150 mm HDPE pipe with 11.4 mm - 14.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2952 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-2999 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2953 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3000 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 160 | 40 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/60/60 | 60 minute | 40 mm - 160 mm HDPE pipe with 3.2 mm - 14.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2954 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3001 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2955 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3002 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2956 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3003 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2957 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3004 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2958 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3005 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2959 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3006 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2960 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3007 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 7.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 7.5 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2961 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3008 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 20 | Up to 1200 x 500 | - | - | - | BB-50, AC, MC | MC160 | -/120/120 | 120 minute | Up to 160 mm uPVC pipe with 2.8 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. The service included 12 mm thick Armaflex lagging, with a 160 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2962 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3009 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2963 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3010 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2964 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3011 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2965 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3012 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2966 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3013 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2967 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3014 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2968 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3015 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | None | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/60 | 60 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2969 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3016 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/45 | 60 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2970 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3017 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC150 | -/60/60 | 60 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2971 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3018 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3 - 4.5 | Up to 1200 x 500 | 13 | - | - | BB-50, AC, FM300, MC | MC32 | -/60/60 | 60 minute | Up to 32 mm PEX pipe with 3.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 13.0 mm deep in 3.0 mm - 4.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2972 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3019 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 118 mm thick walls with 1 layer of 13 mm plasterboard both sides.. | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3 - 4.0 | Up to 1200 x 500 | 13 | - | - | BB-50, AC, FM300, MC | MC32 | -/60/45 | 60 minute | Up to 32 mm PEX-AL-PEX pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 13.0 mm deep in 3.0 mm - 4.0 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2973 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3021 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2974 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3022 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2975 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3023 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2976 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3024 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2977 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3025 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2978 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3026 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 9.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2979 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3027 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 9.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2980 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3028 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 4 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 4.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2981 - SYSTEM DOUBLE UP | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3029 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 2 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/120/45 | 120 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2982 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3030 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 2.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC160 | -/60/60 | 60 minute | Up to 160 mm HDPE pipe with 14.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 2.5 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2983 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3031 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 150 | 40 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/60/60 | 60 minute | 40 mm - 150 mm HDPE pipe with 14.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 9.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2984 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3032 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 150 - 160 | 150 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 9 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | 150 mm - 160 mm HDPE pipe with 14.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 9.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2985 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3033 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 1.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 32 mm PPR pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 1.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2986 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3034 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/90 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2987 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3035 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/90/90 | 90 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2988 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3036 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 12.5 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 12.5 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-2989 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3037 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 - 125 | 110 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 2 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/30/30 | <60 minute | 110 mm - 125 mm PPR pipe with 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 2.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2990 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3038 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 - 160 | 125 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | Size to fit | -/90/90 | 90 minute | 125 mm - 160 mm PPR pipe with 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2991 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3040 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2992 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3041 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 160 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2993 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3042 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 250 | 250 | 250 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC250 | -/120/120 | 120 minute | Up to 250 mm PP/PPR pipe with 6.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 250 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2994 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3043 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC110 | -/120/120 | 120 minute | 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2995 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3044 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | 160 | 160 | 160 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, FM300, MC | MC160 | -/120/120 | 120 minute | 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2996 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3045 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 400 | 400 | 400 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm AAC block wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 0 | Up to 1200 x 500 | - | - | - | MC | MC400 | -/15/15 | <60 minute | 400 mm PE pipe with 8.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. 400 mm BOSS MaxiCollar™ installed on both sides. Tested Capped/Uncapped. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2997 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3046 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | - | - | - | 11 | Up to 1200 x 500 | - | - | - | BB-50, AC, MC | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2998 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3047 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-2999 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3048 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3000 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3049 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3001 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3050 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3002 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3051 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3003 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3052 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3004 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3053 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/120/120 | 120 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3005 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3054 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 6 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/120/120 | 120 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3006 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3055 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/240/240 | 240 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3007 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3056 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/240/240 | 240 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3008 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3057 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3009 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3058 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/240/240 | 240 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3010 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3059 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/240/240 | 240 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3011 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3060 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/240/240 | 240 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3012 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3061 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/240/240 | 240 minute | Up to 150 mm uPVC pipe with 5.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3013 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3062 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/240/240 | 240 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3014 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3063 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 175 mm concrete wall | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 175 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 6 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC150 | -/240/240 | 240 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3015 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3064 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3016 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3065 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3017 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3066 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3018 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3067 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3019 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3068 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3020 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3069 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3021 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3070 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/60/60 | 60 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3022 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3071 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3023 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3072 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3024 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3073 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 100 | 40 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, FM300, MC | Size to fit | -/60/60 | 60 minute | 40 mm - 100 mm HDPE pipe with 2.9 mm - 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. BOSS MaxiCollar™ relative to pipe size, installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3025 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3074 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3026 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3075 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3027 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3076 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3028 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3077 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3029 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3078 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3030 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3079 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC100 | -/90/90 | 90 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3031 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3080 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS Batt™ pattress installed to exposed side of the system. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3032 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3081 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3033 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3082 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed to the exposed side only. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3034 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3083 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.75 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the unexposed side and BOSS FireMastic-HPE™ sealant is used to the exposed side. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed to the exposed side only. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3035 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3084 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | Fill area around pipe | 50 x 96 | 10 | - | - | FM300, MC | MC110 | -/90/90 | 120 minute | Up to 50 mm PP / PP-R pipe with 2.9 mm wall thickness. The pipe was installed at a 30° angle to the separating element through a 50 mm x 96 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 110 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | The BOSS MaxiCollar™ may be extended vertically to fit around the service, provided that the aperture remains fully within the collar. | BF-3036 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3085 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | Fill area around pipe | 156 x 110 | 10 | - | - | FM300, MC | MC160 | -/120/90 | 120 minute | Up to 110 mm uPVC pipe with 6.6 mm wall thickness. The pipe was installed at a 30° angle to the separating element through a 156 mm x 110 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | The BOSS MaxiCollar™ may be extended vertically to fit around the service, provided that the aperture remains fully within the collar. | BF-3037 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3086 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | Fill area around pipe | 156 x 110 | 10 | - | - | FM300, MC | MC160 | -/90/90 | 120 minute | Up to 110 mm PE pipe with 2.7 mm wall thickness. The pipe was installed at a 30° angle to the separating element through a 156 mm x 110 mm aperture. Sealant installed around service 10 mm deep in annular gap finished flush both sides. The system includes a 160 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | The BOSS MaxiCollar™ may be extended vertically to fit around the service, provided that the aperture remains fully within the collar. | BF-3038 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3087 | Plastic_Pipes | Concentric 60/100 plastic pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 60/100 | 60/100 | 60/100 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0 | - | - | - | - | MC | MC110 | -/120/120 | 120 minute | Concentric 60/100 plastic pipe - 101 mm outer pipe with 1.9 mm wall thickness, and 60 mm inner pipe with 2.0 mm wall thickness. The system includes a 110 mm BOSS MaxiCollar™ installed to the exposed side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3039 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3088 | Plastic_Pipes | Concentric c80/120 plastic pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 80/120 | 80/120 | 80/120 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0 | - | - | - | - | MC | MC125 | -/120/120 | 120 minute | Concentric 80/120 plastic pipe - 121 mm outer pipe with 1.5 mm wall thickness, and 82 mm inner pipe with 2.4 mm wall thickness. The system includes a 125 mm BOSS MaxiCollar™ installed to the exposed side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3040 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3089 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 33 | 0 | 33 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0.8 | - | - | - | - | MC | MC40 | -/120/120 | 120 minute | Up to 33.4 mm cPVC pipe with 2.6 mm wall thickness. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3041 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3090 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 42 | 0 | 42 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0.9 | - | - | - | - | MC | MC40 | -/120/90 | 120 minute | Up to 42.2 mm cPVC pipe with 3.3 mm wall thickness. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3042 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3091 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 48 | 0 | 48 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0.85 | - | - | - | - | MC | MC50 | -/120/120 | 120 minute | Up to 48.3 mm cPVC pipe with 3.8 mm wall thickness. The system includes a 50 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3043 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3092 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60 | 0 | 60 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | - | - | - | - | - | 0.85 | - | - | - | - | MC | MC65 | -/120/90 | 120 minute | Up to 60.3 mm cPVC pipe with 4.7 mm wall thickness. The system includes a 65 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3044 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3093 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 6 | - | Depth of collar | - | - | FMHPE, MC | MC32 | -/60/60 | 60 minute | Up to 20 mm PP / PP-R pipe with 4.6 mm wall thickness. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3045 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3094 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 20 | 0 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 10 | - | Depth of collar | - | - | FMHPE, MC | MC32 | -/60/30 | 60 minute | Up to 20 mm PEX pipe with 6.3 mm wall thickness. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3046 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3095 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.5 | - | Depth of collar | - | - | FMHPE, MC | MC40 | -/60/30 | 60 minute | Up to 25 mm PEX pipe with 6.2 mm wall thickness. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 40 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3047 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3096 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.5 | - | Depth of collar | - | - | FMHPE, MC | MC32 | -/60/30 | 60 minute | Up to 25 mm PEX-AL pipe with 5.3 mm wall thickness. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3048 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3097 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | 1 | - | - | - | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | As required | For systems with 2-layers of 13 mm plasterboard on both faces, single layer walls are permitted provided that the area around the penetration is built up with an additional layer of fire rated plasterboard (100 mm x 100 mm from the edge of the aperture. | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3.5 | - | Depth of collar | - | - | FMHPE, MC | MC32 | -/120/60 | 120 minute | Up to 25 mm PEX pipe with 3.1 mm wall thickness. Sealant installed in the gap between the collar and pipe to the full depth of the collar, finished flush both sides. The system includes a 32 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3049 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3098 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 78 mm thick Speedpanel walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 2.5 | - | 10 | 5 | - | FM300, FMHPE, MC | MC150 | -/240/60 | 240 minute | Up to 110 mm uPVC DWV pipe with 3.5 mm wall thickness. FM-300 sealant installed around service 10 mm deep in annular gap finished flush both sides. FM-HPE sealant was also applied as a 5 mm fillet on the joint between the collar and panel both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3050 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3099 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Wall | 78 mm thick Speedpanel walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 2.5 | - | 10 | - | - | FM300, MC | MC150 | -/120/90 | 120 minute | Up to 110 mm uPVC DWV pipe with 3.5 mm wall thickness. FM-300 sealant applied on the joint between the collar and panel both sides. The system includes a 150 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3051 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3100 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Wall | 78 mm thick Speedpanel walls. | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 6 | Up to 1200 x 500 | 10 | - | - | FM300, MC | MC205 | -/240/120 | 240 minute | Up to 160 mm cPVC pipe with 7.7 mm wall thickness. FM-300 sealant applied on the joint between the collar and panel both sides. The system includes a 205 mm BOSS MaxiCollar™ installed to both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3052 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3101 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3053 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3102 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3054 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3103 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3055 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3104 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3056 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3105 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3057 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3106 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC100 | -/120/120 | 120 minute | Up to 100 mm uPVC pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3058 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3107 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3059 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3108 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm PP/PP-MD-PP acoustic pipe with 2.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3060 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3109 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 6 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 110 mm PP/PP-MD-PP acoustic pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 6.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3061 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3110 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 3.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm PP/PPR pipe with 2.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 3.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3062 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3111 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3063 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3112 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC55 | -/90/90 | 90 minute | Up to 50 mm PP/PPR pipe with 1.8 mm - 6.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3064 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3113 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC55 | -/120/120 | 120 minute | Up to 50 mm PP/PPR pipe with 6.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3065 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3114 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/60/60 | 60 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3066 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3115 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC110 | -/15/15 | <60 minute | Up to 110 mm PP/PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3067 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3116 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm PP/PPR pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3068 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3117 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm PP/PPR pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3069 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3118 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm PP/PPR pipe with 4.0 mm - 14.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap on the top side. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3070 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3119 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC55 | -/60/60 | 60 minute | Up to 50 mm PE pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3071 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3120 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC55 | -/45/45 | <60 minute | Up to 50 mm PE pipe with 3.0 mm - 4.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap on both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3072 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3121 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm PE pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3073 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3122 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/30/30 | <60 minute | Up to 110 mm PE pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3074 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3123 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/15/15 | <60 minute | Up to 110 mm PE pipe with 2.7 mm - 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3075 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3124 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm PE pipe with 3.1 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3076 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3125 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3077 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3126 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3078 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3127 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 1.8 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3079 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3128 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC55 | -/90/60 | 90 minute | Up to 50 mm uPVC pipe with 2.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 55 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3080 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3129 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3081 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3130 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3082 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3131 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm uPVC pipe with 4.2 mm - 7.3 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3083 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3132 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/30/30 | <60 minute | Up to 110 mm uPVC pipe with 4.2 mm - 6.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 11.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3084 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3133 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC125 | -/240/240 | 240 minute | Up to 125 mm uPVC pipe with 6.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3085 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3134 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 150 | 0 | 150 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 11 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC150 | -/120/120 | 120 minute | Up to 150 mm uPVC pipe with 5.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 11.0 mm annular gap both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3086 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3135 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm uPVC pipe with 6.2 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3087 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3136 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC50 | -/240/240 | 240 minute | Up to 50 mm HDPE pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3088 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3137 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC110 | -/240/240 | 240 minute | Up to 110 mm HDPE pipe with 10.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 110 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3089 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3138 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC160 | -/240/240 | 240 minute | Up to 160 mm HDPE pipe with 4.9 mm - 9.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 10.0 mm annular gap both sides. 160 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3090 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3139 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides. 110 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3091 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3140 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC160 | -/120/120 | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides. 160 mm BOSS MaxiCollar™ installed on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3092 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3141 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 110 | 0 | 110 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC110 | -/120/120 | 120 minute | Up to 110 mm PP/PPR pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm, installed with 2 90° fittings on the underside to form a U-bend that penetrates the separating element twice. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides for each penetration point. 110 mm BOSS MaxiCollar™ installed on both sides of each penetration point. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3093 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3142 | Plastic_Pipes | PPR | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 160 | 0 | 160 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 10 | Up to 1200 x 500 | 10 | - | - | BB-50, AC, MC, FM300 | MC160 | -/120/- | 120 minute | Up to 160 mm PP/PPR pipe with 4.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm, installed with 2 90° fittings on the underside to form a U-bend that penetrates the separating element twice. Sealant 10.0 mm deep in 10.0 mm annular gap on both sides for each penetration point. 160 mm BOSS MaxiCollar™ installed on both sides of each penetration point. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3094 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3143 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3095 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3144 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC40 | -/60/60 | 60 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3096 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3145 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC50 | -/60/60 | 60 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3097 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3146 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3098 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3147 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC80 | -/60/60 | 60 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3099 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3148 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC100 | -/60/60 | 60 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3100 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3149 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC125 | -/60/60 | 60 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3101 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3150 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3102 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3151 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 - 125 | 40 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300 | Size to fit | -/30/30 | <60 minute | 40 mm to 125 mm HDPE pipe with 3.2 mm - 11.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. BOSS MaxiCollar™ to suit pipe size, installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3103 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3152 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 32 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3104 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3153 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | Up to 40 mm uPVC DWV pipe with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3105 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3154 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC50 | -/120/120 | 120 minute | Up to 50 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3106 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3155 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 65 | 0 | 65 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 65 mm uPVC DWV pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3107 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3156 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | Up to 80 mm uPVC DWV pipe with 2.9 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3108 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3157 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 100 | 0 | 100 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC100 | -/90/90 | 90 minute | Up to 100 mm uPVC DWV pipe with 3.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3109 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3158 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC125 | -/120/120 | 120 minute | Up to 125 mm uPVC DWV pipe with 7.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3110 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3159 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 32 | 0 | 32 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC32 | -/60/60 | 60 minute | Up to 32 mm HDPE pipe with 2.9 mm maximum wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 32 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3111 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3160 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 125 | 0 | 125 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | 12.5 | Up to 1200 x 500 | 5 | - | - | BB-50, AC, MC, FM300, FMHPE | MC125 | -/60/60 | 60 minute | Up to 125 mm HDPE pipe with 11.5 mm maximum wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm. BOSS FireMastic-300™ sealant is used to the top side and BOSS FireMastic-HPE™ sealant is used to the underside. Sealant 5.0 mm deep in 12.5 mm annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3112 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3161 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 78 mm Speedpanel wall | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS OneWay collar | BOSS FireMastic-300™ | - | - | 15 | Up to 1200 x 500 | Full depth | - | - | BB-50, AC, OWC, FM300 | OWC100 | -/120/90 | 120 minute | 100 mm uPVC pipe with 3.3 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm, installed through a 100 mm BOSS OneWay collar centrally located through the separating element. Sealant installed full depth in 15.0 mm annular gap between the 130 mm aperture and the in-wall collar. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3113 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3162 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 130 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS OneWay collar | BOSS FireMastic-300™ | - | - | 27.5 | Up to 1200 x 500 | 25 | - | - | BB-50, AC, OWC, FM300 | OWC100 | -/120/120 | 120 minute | 100 mm uPVC pipe with 3.3 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 1200 mm x 500 mm, installed through a 100 mm BOSS OneWay collar, installed flush with the top of the floor. Sealant installed 25 mm deep in the annular gap between the 155 mm aperture in the separating element, the service and the metal sleeve to the top side. Sealant was also installed 5 mm deep in the annular gap between the separating element, the service and the metal sleeve to the underside. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3114 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3163 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 218 x 74 | 218 x 74 | 218 x 74 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | Up to 600 x 600 | Surface | - | - | BB-50, AC, FM300, UW-25 | 3 layers of UW-25, PWP | -/120/120 | 120 minute | 204 mm x 60 mm uPVC duct with 2.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3115 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3164 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 x 54 | 110 x 54 | 110 x 54 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | Up to 600 x 600 | Surface | - | - | BB-50, AC, FM300, UW-25 | 3 layers of UW-25, PWP | -/15/15 | <60 minute | 110 mm x 54 mm uPVC duct with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3116 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3165 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 220 x 90 | 220 x 90 | 220 x 90 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | - | Up to 600 x 600 | Surface | - | - | BB-50, AC, FM300, UW-25 | 3 layers of UW-25, PWP | -/60/60 | 60 minute | 220 mm x 90 mm uPVC duct with 2.0 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 3 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Sealant applied to the ends of the BOSS UniWrap™ or BOSS PWP Pipe Wrap on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3117 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3166 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 100 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 35 | Up to 600 x 600 | - | 25 (Wall) x 40 (Pipe) | - | BB-50, AC, FM300, UW-25 | 5 layers of UW-25, PWP | -/120/120 | 120 minute | 200 mm uPVC pipe with 7.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 5 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap flush with the face of the separating element on both sides. Fillet of sealant applied 25 mm wide (wall) x 40 mm deep (pipe) on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  | Tested Uncapped/Capped | BF-3118 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3167 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 40 | 0 | 40 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 10 | Up to 600 x 600 | 26 | - | - | BB-50, AC, FM300, UW-25 | 1 layer of UW-25, PWP | -/120/120 | 120 minute | Up to 40 mm uPVC pipe with 2.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 1 layer of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 10.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3119 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3168 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 50 | 0 | 50 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 10 | Up to 600 x 600 | 26 | - | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/120/120 | 120 minute | Up to 50 mm uPVC pipe with 3.5 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 10.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3120 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3169 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 80 | 0 | 80 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 11 | Up to 600 x 600 | 26 | - | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/120/- | 120 minute | Up to 80 mm uPVC pipe with 3.4 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. Sealant 26 mm deep in 11.0 mm annular gap between the wall, service and metal sleeve, finished flush both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3121 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3170 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 33.4 | 0 | 33.4 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 5 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/120/60 | 120 minute | Up to 33.4 mm cPVC pipe with 2.6 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3122 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3171 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 48.3 | 0 | 48.3 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 4.85 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/120/90 | 120 minute | Up to 48.3 mm cPVC pipe with 3.8 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3123 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3172 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 60.3 | 0 | 60.3 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 4.85 | Up to 600 x 600 | - | 5 | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/120/90 | 120 minute | Up to 60.3 mm cPVC pipe with 4.7 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. 5 mm x 5 mm fillet of sealant applied both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3124 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3173 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | Up to 25 | 0 | 25 | Wall | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 116 mm thick walls with 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | 1 | 1 | 1 | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | - | - | 5 | Up to 600 x 600 | - | - | - | BB-50, AC, UW-25 | 2 layers of UW-25, PWP | -/60/60 | 60 minute | Up to 25 mm PEX pipe with 6.2 mm maximum wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap encased in a metal sleeve, flush with the face of the separating element on both sides. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 |  |  | BF-3125 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3174 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 6 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 2.0 mm - 6.9 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3126 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3175 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 12 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 10 layers of UW-25, PWP | -/240/240 | 240 minute | Up to 200 mm PP/PPR pipe with 4.9 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3127 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3176 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 12 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 10 layers of UW-25, PWP | -/120/120 | 120 minute | Up to 200 mm PP/PPR pipe with 4.9 mm - 18.2 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3128 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3177 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 6 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/240/240 | 240 minute | Up to 50 mm PP/PPR pipe with 3.0 - 4.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3129 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3178 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 12 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 10 layers of UW-25, PWP | -/240/240 | 240 minute | Up to 200 mm PP/PPR pipe with 4.9 mm - 18.2 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 10 layers of BOSS UniWrap™ mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3130 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3179 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 6 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 2 layers of UW-25, PWP | -/240/240 | 240 minute | Up to 50 mm uPVC pipe with 2.4 mm - 3.7 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 2 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 6.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3131 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3180 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 12 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 10 layers of UW-25, PWP | -/60/60 | 60 minute | Up to 200 mm uPVC pipe with 7.7 mm - 9.6 mm wall thickness, penetrating 1 layer of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3132 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3181 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 2 layers of 50 mm BOSS Batt™ installed in aperture of designated substrate - Installed in min 150 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS UniWrap™ | BOSS PWP Pipe Wrap | BOSS FireMastic-300™ | - | 12 | Up to 600 x 600 | 10 | - | - | BB-50, AC, FM300, UW-25 | 10 layers of UW-25, PWP | -/240/120 | 240 minute | Up to 200 mm uPVC pipe with 9.6 mm wall thickness, penetrating 2 layers of BOSS Batt™ protecting an aperture up to 600 mm x 600 mm. 10 layers of BOSS UniWrap™ or BOSS PWP Pipe Wrap mid-depth of the floor. Sealant 10.0 mm deep in 12.0 mm annular gap to the top side. | WF FAS 210203 | - | 2025-04-30 | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3133 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3201 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 40 | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | 32 mm uPVC DWV pipe. Sealant 5.0 mm deep in annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3134
BF-3202 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 50 | 5 | - | - | MC, FM300 | MC40 | -/60/60 | 60 minute | 40 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3135
BF-3203 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 65 | 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | 50 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3136
BF-3204 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 65 | 65 | 65 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 80 | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | 65 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3137
BF-3205 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 | 80 | 80 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 90 | 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | 80 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3138
BF-3206 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 115 | 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | 100 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3139
BF-3207 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 150 | 5 | - | - | MC, FM300 | MC125 | -/60/60 | 60 minute | 125 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3140
BF-3208 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 40 | 5 | - | - | MC, FM300 | MC32 | -/60/60 | 60 minute | 32 mm HDPE pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 32 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3141
BF-3209 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 150 | 5 | - | - | MC, FM300 | MC125 | -/30/30 | <60 minute | 125 mm HDPE pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap both sides. 125 mm BOSS MaxiCollar™ installed on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3142
BF-3210 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | 250 x 250 | - | 10 | - | BB, AC, FM300 | - | -/60/60 | 60 minute | Aperture size of 250 mm x 250 mm in the CLT slab. A 252 mm x 252 mm BOSS Batt™ friction fitted into the opening. The BOSS batt is to be recessed 20 mm from the bottom edge of the slab, with a 10 mm x 10 mm fillet of BOSS FireMastic-300™ around the edges on the underside. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3143
BF-3211 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 110 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 110 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 | 25 | - | - | FMHPE | - | -/60/60 | 60 minute | 5 x 2.5mm² TPS cables, 5 x fire alarm cables and 5 x Cat6 cables, installed through a 50 mm core hole in the CLT slab. The aperture of the cables are filled on both sides of the slab with BOSS FireMastic-HPE™ sealant to a depth of 25 mm. | 147941.00FTR 1024 (V2.3) | - | 2024-12-19 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3144
BF-3212 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 40 | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | 32 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 40 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3145
BF-3213 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 50 | 5 | - | - | MC, FM300, FMHPE | MC40 | -/120/120 | 120 minute | 40 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 40 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3146
BF-3214 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 65 | 5 | - | - | MC, FM300, FMHPE | MC50 | -/120/120 | 120 minute | 50 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 50 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3147
BF-3215 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 65 | 65 | 65 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 80 | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | 65 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 80 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3148
BF-3216 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 | 80 | 80 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 90 | 5 | - | - | MC, FM300, FMHPE | MC80 | -/120/120 | 120 minute | 80 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 80 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3149
BF-3217 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 115 | 5 | - | - | MC, FM300, FMHPE | MC100 | -/90/90 | 90 minute | 100 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 100 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3150
BF-3218 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 150 | 5 | - | - | MC, FM300, FMHPE | MC125 | -/120/120 | 120 minute | 125 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 125 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3151
BF-3219 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 40 | 5 | - | - | MC, FM300, FMHPE | MC40 | -/60/60 | 60 minute | 32 mm HDPE pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 32 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3152
BF-3220 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 150 | 5 | - | - | MC, FM300, FMHPE | MC125 | -/60/60 | 60 minute | 125 mm HDPE pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side. BOSS FireMastic-HPE™ sealant 5.0 mm deep in annular gap on the underside. 125 mm BOSS MaxiCollar™ installed on the underside. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3153
BF-3221 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | 250 x 250 | - | 5 | - | BB, AC, FM300 | - | -/120/120 | 120 minute | 250 mm x 250 mm aperture in the CLT slab. Two layers of 252 mm x 252 mm BOSS Batt™ are to be friction-fitted into the opening, recessed 20 mm from the bottom face of the slab. A 50 mm wide x 50 mm thick strip of BOSS Batt™ is to be installed between the two BOSS Batt™ layers around the perimeter. A 5 mm x 5 mm fillet of BOSS FireMastic-300™ is applied around the edge of the batt on the underside of the slab. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3154
BF-3222 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 200 mm CLT floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 200 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 | 25 | - | - | FMHPE | - | -/120/120 | 120 minute | 5 x 2.5mm² TPS cables, 5 x fire alarm cables and 5 x Cat6 cables, installed through a 50 mm core hole in the CLT slab. The aperture of the cables are filled on both sides of the slab with BOSS FireMastic-HPE™ sealant to a depth of 25 mm. | 147942.00FTR 1024 (V2.2) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3155
BF-3223 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | - | - | - | - | - | 250 x 250 | - | 5 | - | BB, FM300 | - | -/60/60 | 60 minute | 250 mm x 250 mm aperture in the ceiling system. A layer of 252 mm x 252 mm BOSS Batt™ is friction-fitted within the opening of the timber framing, installed with the underside of the BOSS Batt™ to the top of the ceiling plasterboard lining. A 5 mm x 5 mm fillet of BOSS FireMastic-300™ is applied around the edge of the BOSS Batt™ at the interface of the framing on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3156 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3224 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 25 | Top - no sealant Bottom 16 | - | - | FM300 | - | -/60/60 | 60 minute | A 25 mm diameter core hole was made through the ceiling system. BOSS FireMastic-300™ sealant was installed within the plasterboard to fill the full opening to a depth of 16 mm. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3157 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3225 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 60 | Top and bottom 5 | - | - | MC, FM300 | MC50 | -/60/60 | 60 minute | 50 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3158 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3226 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 65 | 65 | 65 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 73 | Top and bottom 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | 65 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3159 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3227 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 | 80 | 80 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 85 | Top and bottom 5 | - | - | MC, FM300 | MC80 | -/60/60 | 60 minute | 80 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3160 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3228 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 112 | Top and bottom 5 | - | - | MC, FM300 | MC100 | -/60/60 | 60 minute | 100 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3161 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3229 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 121 | Top 5 and Bottom 16 | - | - | FM300 | - | -/60/45 | 60 minute | 100 mm steel pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side, and 16 mm on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3162 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3230 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 40 | Top 5 and Bottom 16 | - | - | FM300 | - | -/60/60 | 60 minute | 32 mm steel pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on the top side, and 16 mm on the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3163 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3231 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | Yes | 13 mm thick fire rated plasterboard pattress | BOSS FireMastic-300™ | - | - | - | - | - | - | 25 | Top 5 and Bottom 29 | - | - | FM300 | - | -/60/60 - RISF 64 min | 60 minute | Bundle of 4 x Fire Alarm cables. A 13 mm thick pattress of fire rated plasterboard was installed to the underside of the penetration. BOSS FireMastic-300™ sealant in annular gap to depth of the plasterboard (29 mm) on the underside. 1 mm thick backcoat of FireMastic-300™ sealant 50 mm along the cables within the floor cavity. BOSS FireMastic-300™ sealant 5 mm deep in the annular gap on the top side. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3164 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3232 | Data_Comms_Cables_Inc_Bundles_and_Trays | COAX | Service Penetration | Electrical | - | - | - | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | Yes | 13 mm thick fire rated plasterboard pattress | BOSS FireMastic-300™ | - | - | - | - | - | - | 25 | Top 5 and Bottom 29 | - | - | FM300 | - | -/60/60 - RISF 64 min | 60 minute | Bundle of 4 x COAX cables. A 13 mm thick pattress of fire rated plasterboard was installed to the underside of the penetration. FireMastic-300™ sealant in annular gap to depth of the plasterboard (29 mm) on the underside. 1 mm thick backcoat of FireMastic-300™ sealant 50 mm along the cables within the floor cavity. BOSS FireMastic-300 sealant 5 mm deep in the annular gap on the top side. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3165 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3233 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Ceiling | 1 layer of 16 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 225 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 64 | - | - | - | ALX | - | -/60/15 | 60 minute | 90 mm x 50 mm BOSS ALX75™ installed in a 64 mm wide linear gap. A gap 90 mm wide is created through the system, lined with 13 mm fire rated plasterboard to the timber framing to create a 64 mm wide linear gap. The BOSS ALX75™ strip is friction fitted flush with the underside. | 147943.00 FTR (V2.4) | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3166 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3234 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 37 | 5 | - | - | MC, FM300 | MC40 | -/240/180 | 240 minute | 32 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3167
BF-3235 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 47 | 5 | - | - | MC, FM300 | MC40 | -/240/180 | 240 minute | 40 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3168
BF-3236 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 62 | 5 | - | - | MC, FM300 | MC50 | -/240/180 | 240 minute | 50 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 50 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3169
BF-3237 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 65 | 65 | 65 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 77 | 5 | - | - | MC, FM300 | MC80 | -/240/180 | 240 minute | 65 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3170
BF-3238 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 80 | 80 | 80 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 84 | 5 | - | - | MC, FM300 | MC80 | -/240/180 | 240 minute | 80 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 80 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3171
BF-3239 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 120 | 5 | - | - | MC, FM300 | MC100 | -/240/180 | 240 minute | 100 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3172
BF-3240 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 150 | 150 | 150 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 172 | 5 | - | - | MC, FM300 | MC150 | -/240/180 | 240 minute | 150 mm uPVC DWV pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 150 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3173
BF-3241 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 and 25 | 20 | 25 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 60 | Top 10 and Bottom 25 | - | - | FMHPE | - | -/240/180 | 240 minute | uPVC conduit bundle incorporating 2 x 20 mm and 1 x 25 mm diameter conduits. BOSS FireMastic-HPE™ sealant 25 mm deep in the annular gap on the underside and 10 mm deep on the top side. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3174
BF-3242 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20, 25 and 32 | 20 | 32 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 80 | Top 10 and Bottom 25 | - | - | FMHPE | - | -/240/210 | 240 minute | uPVC conduit bundle incorporating 1 x 20 mm, 1 x 25 mm and 1 x 32 mm diameter conduits. BOSS FireMastic-HPE™ sealant 25 mm deep in the annular gap on the underside and 10 mm deep on the top side. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3175
BF-3243 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20, 25 and 32 | 20 | 32 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 100 | Top 10 and Bottom 25 | - | - | FMHPE | - | -/240/150 | 240 minute | uPVC conduit bundle incorporating 2 x 20 mm, 2 x 25 mm and 2 x 32 mm diameter conduits. BOSS FireMastic-HPE™ sealant 25 mm deep in the annular gap on the underside and 10 mm deep on the top side. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3176
BF-3244 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 47 | 5 | - | - | MC, FM300 | MC40 | -/240/150 | 240 minute | 40 mm Valsir TriPlus pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 40 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3177
BF-3245 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | - | 112 | 5 | - | - | MC, FM300 | MC150 | -/240/180 | 240 minute | 110 mm Valsir TriPlus pipe. BOSS FireMastic-300™ sealant 5.0 mm deep in annular gap on both sides. 100 mm BOSS MaxiCollar™ installed on the underside. | 148693.00 FTR V2.3 | - | 2024-11-14 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3178
BF-3246 | Water_Valves_and_Tap Sets | - | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 17.7 | 45.9 | 13 | - | - | FM300 | - | -/60/60 | 60 minute | 1 - sided penetration. 20 mm x 1/2" External Wingback Elbow (Brass) penetrating the wall from either direction. Wingback fixed to a 300 mm wide x 200 mm high x 20 mm thick plywood backing. BOSS FireMastic-300™ sealant 13 mm deep in the annular gap finished flush. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3179 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3247 | Water_Valves_and_Tap Sets | - | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 11.1 - 13.1 | 45.2 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 1 - sided penetration. 20 mm x 1/2" External Wingback Elbow (Brass) penetrating the wall from either direction. Wingback fixed to a 300 mm wide x 200 mm high x 20 mm thick plywood backing. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap finished flush. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3180 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3248 | Water_Valves_and_Tap Sets | - | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireSilicone-EMA™ | - | - | - | - | - | 8.7 - 15.6 | 45.3 | 13 | - | - | FMEMA | - | -/60/60 | 60 minute | 1 - sided penetration. 20 mm x 1/2" External Wingback Elbow (Brass) penetrating the wall from either direction. Wingback fixed to a 300 mm wide x 200 mm high x 20 mm thick plywood backing. BOSS FireMastic-EMA™ sealant 13 mm deep in the annular gap finished flush. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3181 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3249 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | - | 67.9 | Fill collar | - | - | MC SHELL, FMHPE | MC65 Shell | -/60/45 | 60 minute | Bundle of 22 x 2C+E 2.5mm² TPS cables. A 65 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the cables, finished flush with the surface of the collar. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3182 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3250 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | - | 69 | Fill collar | - | - | MC SHELL, FMHPE | MC65 Shell | -/60/60 | 60 minute | Bundle of 38 x CAT6 cables. A 65 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the cables, finished flush with the surface of the collar. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3183 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3251 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 |  | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 8.0 - 12.4 | 45.5 | 13 | 20 | - | FMHPE | - | -/60/15 | 60 minute | 25 mm PEX pipe with 2.95 mm wall thickness. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap with 20 mm x 20 mm fillet of sealant applied both sides. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3252 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 20.2 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 2C Heat Trace Cable, 13.6 mm wide x 6.4 mm deep. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3185 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3253 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 20.2 | 13 | - | - | FM300 | - | -/60/60 | 60 minute | 2C Heat Trace Cable, 13.6 mm wide x 6.4 mm deep. BOSS FireMastic-300™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25011-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3186 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3254 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | - | 52.5 | Fill collar | - | - | MC SHELL, FMHPE | MC50 Shell | -/60/60 | 60 minute | Cable bundle of: • 8 x CAT6 cables • 8 x COAX • 8 x Fire alarm cables A 50 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the cables, finished flush with the surface of the collar. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3187 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3255 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 6.2 - 14.5 | 79.3 | 13 | - | - | FMHPE | - | -/60/45 | 60 minute | 32 mm copper pipe with 1.65 mm wall thickness, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-300™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3188 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3256 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 5.7 - 8.3 | 60.5 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 20 mm PEX pipe with 3.05 mm wall thickness, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3189 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3257 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 7.5 - 11.6 | 70.1 | 13 | - | - | FMHPE | - | -/30/30 | <60 minute | 25 mm PEX pipe with 2.95 mm wall thickness, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3190 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3258 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 7.8 - 8.9 | 85.9 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 25 mm uPVC condensate pipe with 1.95 mm wall thickness, insulated with 19 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3191 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3259 | Mixed_Trades-Mixed_services_in_same aperture | - | Service Penetration | Mixed Trades | 60 | 60 | 60 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 7.3 - 12.4 | 73.3 | 13 | 30 (Wall) x 50 (services) | - | FM300 | - | -/60/60 | 60 minute | Services bundle including: • 60 mm Steel pipe with 3.45 mm wall thickness • 2 Fire Alarm Cables BOSS FireMastic-300™ sealant 13 mm deep in the annular gap with 30 mm (Wall) x 50 mm (Services) fillet of sealant applied both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3192 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3260 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 60 | 60 | 60 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 8.5 - 10.8 | 73.3 | 13 | - | - | FM300 | - | -/60/30 | 60 minute | 60 mm Steel pipe with 3.45 mm wall thickness. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3193 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3261 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20, 25 and 32 | 20 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 70.1 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | uPVC conduit bundle incorporating 1 x 20 mm, 1 x 25 mm and 1 x 32 mm diameter conduits. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3194 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3262 | Power_Cables_Inc_Bundles_and_Trays | Aluminium Core | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 3.9 - 8.4 | 34.6 | 13 | - | - | FMHPE | - | -/60/30 | 60 minute | Nexans Cable - 22.5 mm diameter, 185 mm2 1C AL/PVC/XLPE electrical cable. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3195 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3263 | Power_Cables_Inc_Bundles_and_Trays | Aluminium Core | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 4.1 - 7.9 | 29 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | Nexans Cable - 16.95 mm diameter, 95 mm2 1C AL/PVC/XLPE electrical cable. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25012-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3196 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3264 | Mixed_Trades-Mixed_services_in_same aperture | - | Service Penetration | Mixed Trades | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 5.1 - 8.3 | 60.6 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 20 mm copper pipe with 1.0 mm wall thickness, incorporating a Heat Trace Cable, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3197 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3265 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 5.8 - 7.6 | 59.8 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 20 mm PEX pipe with 3.05 mm wall thickness, incorporating a Heat Trace Cable, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3198 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3266 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 3.6 - 8.9 | 92.1 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | HVAC Bundle: • 1 x 19.05 mm + 9.52 mm Paircoil with 13 mm insulation • 1 x 2C 1.5 mm2 Control cable • 1 x 2C + E 2.5 mm2 TPS cable • 1 x 20 mm x 2.0 mm wall thickness uPVC Condensate drain. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap with 15 mm x 15 mm fillet of sealant applied both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3199 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3267 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 2.5 - 7.3 | 109.8 | 13 | 15 | - | FMHPE | - | -/60/30 | 60 minute | HVAC Bundle: • 1 x 19.05 mm + 9.52 mm Paircoil with 25 mm insulation • 1 x 2C 1.5 mm2 Control cable • 1 x 2C + E 2.5 mm2 TPS cable • 1 x 20 mm x 2.0 mm wall thickness uPVC Condensate drain. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap with 15 mm x 15 mm fillet of sealant applied both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3200 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3268 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | 4.6 - 8.9 | 137.2 | Fill collar | - | - | MC SHELL, FMHPE | MC150 Shell | -/60/60 | 60 minute | HVAC Bundle: • 1 x 32 mm + 25 mm copper pipes with 19 mm insulation • 1 x 2C 1.5 mm2 Control cable • 1 x 2C + E 2.5 mm2 TPS cable • 1 x 20 mm x 2.0 mm wall thickness uPVC Condensate drain. A 150 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the services, finished flush with the surface of the collar. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3201 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3269 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | 2.1 - 10.4 | 137.4 | Fill collar | - | - | MC SHELL, FMHPE | MC150 Shell | -/60/60 | 60 minute | HVAC Bundle: • 2 x 19.05 mm + 9.52 mm Paircoil with 19 mm insulation • 2 x 2C 1.5 mm2 Control cable • 2 x 2C + E 2.5 mm2 TPS cable • 2 x 20 mm x 2.0 mm wall thickness uPVC Condensate drain. A 150 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the services, finished flush with the surface of the collar. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3202 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3270 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 8.2 - 9.0 | 93.2 | 13 | 30 (Wall) x 50 (services) | - | FM300 | - | -/60/60 | 60 minute | 60 mm Steel pipe with 3.45 mm wall thickness. BOSS FireMastic-300™ sealant 13 mm deep in the annular gap with 30 mm (Wall) x 50 mm (Services) fillet of sealant applied both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3203 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3271 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 and 25 | 20 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 4.2 - 7.0 | 61.3 | 13 | - | - | FMHPE | - | -/60/30 | 60 minute | uPVC conduit bundle incorporating 2 x 20 mm and 1 x 25 mm diameter conduits. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap finished flush both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3204 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3272 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 14.2 - 18.8 | 117.2 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 32 mm copper pipe with 1.65 mm wall thickness, insulated with 25 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25013-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3205 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3273 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 8.6 - 9.8 | 52.2 | 13 | 15 | - | FMHPE | - | -/60/60 | 60 minute | 25 mm cPVC pipe with 2.9 mm wall thickness. BOSS FireMastic-HPE™ sealant 13 mm deep in the annular gap with 15 mm x 15 mm fillet of sealant applied both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3206 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3274 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 4.8 - 7.1 | 65.1 | 13 | - | - | FM300 | - | -/60/0 | 60 minute | 50 mm copper pipe with 1.9 mm wall thickness. BOSS FireMastic-300™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3207 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3275 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 8.2 - 12.3 | 61.6 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 15 mm copper pipe with 1.8 mm wall thickness, insulated with 13 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3208 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3276 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS MaxiCollar™ Shell | BOSS FireMastic-HPE™ | - | - | - | - | 8.7 - 9.8 | 78.7 | Fill collar | - | - | MC SHELL, FMHPE | MC80 Shell | -/60/60 | 60 minute | 50 mm cPVC pipe with 5.3 mm wall thickness. An 80 mm BOSS MaxiCollar™ (Shell only) to both sides of the wall. BOSS FireMastic-HPE™ sealant to the full depth of the collar around the services, finished flush with the surface of the collar. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3209 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3277 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 13.7 - 16.0 | 82.8 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 15 mm copper pipe with 1.8 mm wall thickness, insulated with 19 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3210 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3278 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 16.8 - 18.5 | 107.5 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 32 mm copper pipe with 1.65 mm wall thickness, insulated with 19 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3211 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3279 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 13.8 - 16.3 | 109.2 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 15 mm copper pipe with 1.8 mm wall thickness, insulated with 32 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3212 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3280 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 10.5 - 12.4 | 121.1 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 32 mm copper pipe with 1.65 mm wall thickness, insulated with 32 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3213 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3281 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 12.4 - 14.7 | 92.2 | 13 | - | - | FMHPE | - | -/60/60 | 60 minute | 15 mm copper pipe with 1.8 mm wall thickness, insulated with 25 mm thick nitrile insulation. BOSS FireMastic-HPE™ sealant 13 mm deep in annular gap finished flush both sides. | FTSL-PF25014-R2 | - | 2025-04-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3214 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3282 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 150 | 150 | 150 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 10 | 170 | 26 | 20 | - | FM300 | - | -/120/0 | 120 minute | 150 mm copper pipe with 2.0 mm wall thickness. BOSS FireMastic-300™ sealant 26 mm deep in the annular gap with 20 mm x 20 mm fillet of sealant applied both sides. | FRT180472 R2.0 | - | 8/05/20219 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3215 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3283 | Other | GPO | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS UniWrap™ | - | - | - | - | - | 2 | 99 x 55 | - | - | - | UW | - | -/120/120 | 120 minute | 95 mm wide x 50 mm high x 50 mm deep steel wallbox installed behind the 116 mm x 75 mm GPO, with the cable penetrating the hole on the top of the wallbox. A 2 mm thick x 40 mm wide strip of BOSS UniWrap™ was installed internally on the back face of the wallbox. | FRT180472 R2.0 | - | 8/05/20219 | None | AS 1530.4:2014 | AS 4072.1-2005 | - | Approval from Unexposed side | BF-3216 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3284 | Other | GPO | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS UniWrap™ | - | - | - | - | - | 2 | 99 x 55 | - | - | - | UW | - | -/120/90 | 120 minute | 95 mm wide x 50 mm high x 50 mm deep steel wallbox installed behind the 116 mm x 75 mm GPO, with the cable penetrating the hole on the top of the wallbox. A 2 mm thick x 40 mm wide strip of BOSS UniWrap™ was installed internally on the back face of the wallbox. | FRT180472 R2.0 | - | 8/05/20219 | None | AS 1530.4:2014 | AS 4072.1-2005 | - | Approval from Exposed side | BF-3217 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3285 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 10 | 80 | 26 | 50 | - | FM300 | - | -/120/120 | 120 minute | 50NB Galvanised steel sprinkler pipe with 3.7 mm wall thickness. BOSS FireMastic-300™ sealant 26 mm deep in annular gap with 50 mm x 50 mm fillet of sealant applied both sides. | FRT180472 R2.0 | - | 8/05/20219 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3218 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3286 | Power_Cables_Inc_Bundles_and_Trays | Aluminium Core | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS CableTransit™ | - | - | - | 4 | 110 x 110 | 25 | - | - | BB, FM300, CT | CT120 | -/120/30 | 120 minute | Bundle of Aluminium cables, consisting of: • 2 x Aluminium cables with 70 mm2 conductor • 2 x Aluminium cables with 120 mm2 conductor • 2 x Aluminium cables with 185 mm2 conductor • 2 x Aluminium cables with 240 mm2 conductor Cables were installed through a BOSS Cable Transit™ (CT120) positioned within a 110 mm x 110 mm opening in both the BOSS Batt™ and the substrate. The interface between the BOSS Batt™ and the substrate was sealed with 2 mm of BOSS FireMastic-300™. The annular gap of the CT120 was sealed with BOSS FireMastic-300™ sealant 25 mm deep on both sides. | FRT180473 R1.0 | - | 2019-05-31 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3219 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3287 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 10 | 80 | 10 | 50 | - | FM300 | - | -/120/90 | 120 minute | 50NB Galvanised steel sprinkler pipe with 3.7 mm wall thickness. BOSS FireMastic-300™ sealant 10 mm deep in annular gap with 50 mm x 50 mm fillet of sealant applied both sides. | FRT180473 R1.0 | - | 2019-05-31 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3220 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3288 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 16 | Top 19 Bottom 26 | - | - | FM300 | - | -/90/90 - RISF 36 min | 90 minute | Bundle of 2 x 2.5 mm², 2C+E TPS Power Cables. BOSS FireMastic-300™ sealant 26 mm deep in annular gap of plasterboard finished flush on the underside. BOSS FireMastic-300™ sealant 19 mm deep in annular gap of particle board flooring on the top side, finished flush. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3221 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3289 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 44 | Top 19 Bottom 26 | - | - | FM300 | - | -/90/90 - RISF 60 min | 90 minute | Bundle of 7 x CAT6 cables. The cable bundle was installed through a steel spring 28 mm diameter x 180 mm long of 1.6 mm thick steel, that was installed flush with the underside of the ceiling. BOSS FireMastic-300™ sealant 26 mm deep in annular gap of plasterboard finished flush on the underside. BOSS FireMastic-300™ sealant 19 mm deep in annular gap of particle board flooring on the top side, finished flush. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3222 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3290 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-300™ | BOSS UniWrap™ | BOSS Thermal Defence Wrap | - | - | - | - | 51 | Top 19 Bottom Surface | - | - | FM300, UW, TDW | - | -/90/90 - RISF 35 min | 90 minute | 32NB medium steel sprinkler pipe with 3.0 mm wall thickness. 105 mm high x 6 mm thick BOSS Thermal Defence Wrap inside the ceiling cavity, flush with the underside of the ceiling system. A layer of 2 mm thick BOSS UniWrap™ flush with the underside of the ceiling system around the BOSS Thermal Defence Wrap. BOSS FireMastic-300™ sealant applied as a surface sealant in the annular gap on the underside as a smoke seal. BOSS FireMastic-300™ sealant 19 mm deep in annular gap of particle board flooring on the top side, finished flush. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3223 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3291 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 51 | Top 19 Bottom 26 | - | - | FM300 | - | -/90/90 - RISF 54 min | 90 minute | 10.6 mm diameter Main power cable. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap of plasterboard finished flush on the underside. BOSS FireMastic-300™ sealant 19 mm deep in annular gap of particle board flooring on the top side, finished flush. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3224 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3292 | Mixed_Trades-Mixed_services_in_same aperture | - | Service Penetration | Mixed Trades | 25 | 25 | 25 | Ceiling | 2 layers of 13 mm FR plasterboard fixed to 190 mm x 45 mm timber framing with 19 mm thick particle board flooring to the top side | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | 235 | None | NA | BOSS FireMastic-300™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 51 | Top 19 Bottom 26 | - | - | FM300, MC, FMHPE | MC65 | -/90/90 - RISF 24 min | 90 minute | Bundle consisting of: • 2 x 25 mm uPVC conduits with 2 mm wall thickness • 2 x 2.5 mm², 2C+E TPS Power Cables 65 mm BOSS MaxiCollar™ installed to the underside of the ceiling system. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap of plasterboard finished flush on the underside. BOSS FireMastic-300™ sealant 19 mm deep in annular gap of particle board flooring on the top side, finished flush. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3225 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3293 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | 11.5 | 76 | Top 5 Bottom 25 | - | - | BB, FMHPE | - | -/120/120 | 120 minute | Bundle of 22 x 2.5 mm², 2C+E TPS Power Cables. 270 mm x 270 mm section of BOSS Batt™ installed to the underside of the floor system, with the gap between the BOSS Batt™ and the top rib filled with a trapezoid shape section of BOSS Batt™. BOSS FireMastic-HPE™ sealant to depth of 5 mm on the top side finished flush. BOSS FireMastic-HPE™ 25 mm deep in the annular gap on the underside finished flush. | FRT180137 R2.0 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3226 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3294 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 130 mm thick concrete floor. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | 11.5 | 76 | Top 5 Bottom 25 | - | - | BB, FMHPE | - | -/120/120 | 120 minute | Bundle of 22 x 2.5 mm², 2C+E TPS Power Cables. 270 mm x 270 mm section of BOSS Batt™ installed to the underside of the floor system. BOSS FireMastic-HPE™ sealant to depth of 5 mm on the top side finished flush. The annular gap on the underside was filled with BOSS FireMastic-HPE™ 25 mm deep finished flush. | FRT180137 R2.0 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3227 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3295 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 24 | 78 | 25 | - | - | FMHPE | - | -/120/0 | 120 minute | 32 mm PEX-a pipe with 5.4 mm wall thickness. BOSS FireMastic-HPE™ sealant 25 mm deep in annular gap finished flush both sides. | FRT180137 R2.0 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3228 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3296 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 1 | 34 | 25 | 10 | - | FM300 | - | -/120/30 | 120 minute | 32 mm copper pipe with 1.3 mm wall thickness. BOSS FireMastic-300™ sealant 25 mm deep in the annular gap with 10 mm x 10 mm fillet of sealant applied both sides. | FRT180137 R2.0 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3229 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3297 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 50 | 25 | - | - | FMHPE | - | -/240/240 | 240 minute | 2 x 20 mm diameter uPVC conduits with 2.0 mm wall thickness. BOSS FireMastic-HPE™ sealant 25 mm deep in the annular gap on both sides. | FRT220049 R1.2 | - | 2022-12-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3230
BF-3298 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 34 | 34 | 34 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 4 | 42 | 26 | 50 | - | FM300 | - | -/120/120 | 120 minute | 34 mm diameter (25NB) galvanised steel sprinkler pipe with 3.5 mm wall thickness. BOSS FireMastic-300™ sealant 26 mm deep in the annular gap with 50 mm x 50 mm fillet of sealant applied both sides. | FRT180474 R3.0 | - | 2020-02-26 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3231 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3299 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 3.5 | 30 | 26 | 30 | - | FM300 | - | -/120/120 | 120 minute | Bundle of 7 x 2.5 mm², 2C+E TPS Power Cables. BOSS FireMastic-300™ sealant 26 mm deep in the annular gap with 30 mm x 30 mm fillet of sealant applied both sides. | FRT190033 R1.0 | - | 2019-02-27 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3232 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3300 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | BOSS CableTransit™ | - | - | - | - | 105 | - | - | 300 | FM300, P40MAK, CT | CT120 | -/120/120 | 120 minute | Bundle of the following services: • 1 × 16 mm² 2C+E cable • 4 × 2.5 mm2 2C+E TPS cable • 6 × RG6 Coax cables • 10 × CAT6 cables • 4 × 2.5 mm2 3C+E cables • 6 × 4 Core security cables • 1 × Ø20 mm uPVC pipe • 2 × 10 mm2 2C+E power cables Services installed through a BOSS Cylindrical Cable Transit™ (CT120) within a 105 mm aperture. The annular gap of the CT120 was sealed with BOSS FireMastic-300™ sealant 5 mm deep on both sides finished flush. 300mm wide BOSS P40-MAK Wrap™ around services on both sides. | FRT210322 R1.1 | - | 2022-06-30 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3233 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3301 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 75 mm thick Hebel wall | - | - | - | 1 | 1 | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 75 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 60 | - | - | - | FM300 | - | -/120/120 | 120 minute | 32NB medium steel sprinkler pipe with 4.3 mm wall thickness. BOSS FireMastic-300™ sealant 10 mm deep in the annular gap with 30 mm x 30 mm fillet of sealant applied both sides. | FRT210322 R1.1 | - | 2022-06-30 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3234 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3302 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 137 mm thick CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 137 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1.8 | 24 | Depth of collar | - | - | MC, FM300 | MC65 | -/90/90 | 90 minute | 20mm PEX-a pipe with 2.8 mm wall thickness. A 25 mm BOSS MaxiCollar™ to both sides of the wall. BOSS FireMastic-300™ sealant to the full depth of the collar around service, finished flush with the surface of the collar. | EWFA 54783400.1 | - | 2018-07-11 | None | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Capped/Capped | BF-3235 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3303 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 137 mm thick CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 137 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 14.8 | 45 | 25 | - | - | FM300 | - | -/90/90 | 90 minute | Bundle of 3 x CAT6 cables. BOSS FireMastic-300™ sealant 25 mm deep in annular gap finished flush both sides. | EWFA 54783400.1 | - | 2018-07-11 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3236 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3304 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 137 mm thick CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 137 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | 9.3 | 45 | 25 | - | - | FM300 | - | -/90/90 | 90 minute | Bundle of 5 x 2.5 mm², 2C+E TPS Power Cables. BOSS FireMastic-300™ sealant 25 mm deep in the annular gap with 5 mm x 5 mm fillet of sealant applied both sides. | EWFA 54783400.1 | - | 2018-07-11 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3237 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3305 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 137 mm thick CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 137 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 12.3 | 60 | 25 | - | - | FMHPE | - | -/90/90 | 90 minute | 20 mm PEX-a pipe with 2.8 mm wall thickness. BOSS FireMastic-HPE™ sealant 25 mm deep in annular gap finished flush both sides. | EWFA 54783400.1 | - | 2018-07-11 | None | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Capped/Capped | BF-3238 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3306 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 48 | 48 | 48 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | - | 58 | - | 5 | - | UW, FM300 | - | -/120/90 | 120 minute | 40 mm cPVC pipe with 3.8 mm wall thickness. 2 layers of BOSS UniWrap™ flush with the face of the separating element on both sides. BOSS FireMastic-300™ sealant applied to the resulting gap with a 5 mm x 5 mm fillet on both sides. | FSP 1846 Rev B | - | 2017-11-06 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3239 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3307 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 33 | 33 | 33 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | - | 58 | - | 5 | - | UW, FM300 | - | -/120/60 | 120 minute | 33.4 mm cPVC pipe with 2.6 mm wall thickness. 2 layers of BOSS UniWrap™ flush with the face of the separating element on both sides. BOSS FireMastic-300™ sealant applied to the resulting gap with a 5 mm x 5 mm fillet on both sides. | FSP 1846 Rev B | - | 2017-11-06 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3240 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3308 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | - | 70 | - | 5 | - | UW, FM300 | - | -/120/90 | 120 minute | 50 mm cPVC pipe with 4.7 mm wall thickness. 2 layers of BOSS UniWrap™ flush with the face of the separating element on both sides. BOSS FireMastic-300™ sealant applied to the resulting gap with a 5 mm x 5 mm fillet on both sides. | FSP 1846 Rev B | - | 2017-11-06 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3241 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3309 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 13 | - | 50 | - | FM300 | - | -/90/90 | 90 minute | Single 2.5 mm², 2C+E TPS Power Cable. BOSS FireMastic-300™ sealant as a surface seal around the cable with 50 mm x 50 mm fillet of sealant applied both sides. | FSP 1833 Rev D | - | 2017-06-28 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3242 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3310 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 150 wide x 100 high | - | 50 | 300 | FM300, P40MAK | - | -/90/90 | 90 minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables, installed onto a 150 mm wide tray. The system to be installed within a 150 mm wide x 100 mm high aperture sealed with 50 mm x 50 mm fillet of BOSS FireMastic-300™ on both sides. 2 layers of BOSS P40-MAK Wrap™ wrapped around the system 300 mm on both sides from the sealant edge. | FSP 1833 Rev D | - | 2017-06-28 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3243 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3311 | Power_Cables_Inc_Bundles_and_Trays | Appendix D1 Config | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 16 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96 | None | NA | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 300 wide x 40 high | - | 50 | 300 | FM300, P40MAK | - | -/90/90 | 90 minute | Partial Appendix D1 Group A cable configuration, consisting of: - 3 x 3C+E 6 mm² cables - 8 x 3C+E 16 mm² cables Cable installed onto a 300 mm wide cable tray. The system installed within a 300 mm wide x 40 mm high aperture sealed with 50 mm x 50 mm fillet of BOSS FireMastic-300™ on both sides. 2 layers of BOSS P40-MAK Wrap™ wrapped around the system 300 mm on both sides from the sealant edge. | FSP 1833 Rev D | - | 2017-06-28 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3244 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3312 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 130 mm thick CLT wall | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | 130 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 73 | 10 | 30 | - | FM300 | - | -/90/60 | 90 minute | 50NB Galvanised steel sprinkler pipe with 3.3 mm wall thickness. BOSS FireMastic-300™ sealant 10 mm deep in annular gap with 30 mm x 30 mm fillet of sealant applied both sides. | FRT210330 R1.1 | - | 2022-11-12 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3245 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3313 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | 84 | Depth of collar | - | - | BB, AC, MC, FMHPE | MC100 | -/120/90 | 120 minute | HVAC Bundle - 3 x 3/8" x 3/4" Paircoils with 13 mm thick FR lagging - 0.8 mm / 1.1 mm thick pipe wall thickness. An additional 320 mm x 320 mm pattress of BOSS Batt™ was installed to the main BOSS Batt™ fire protection, with a 10 mm bead of FireMastic-HPE™ to the perimeter. 100 mm BOSS MaxiCollar™ installed on both sides. BOSS FireMastic-HPE™ sealant to the full depth of the collar around service, finished flush with the surface of the collar on both sides. | FRT190428 R1.0 | - | 2019-12-24 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3246 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3314 | Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 324 | 324 | 324 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 486 | 5 | - | Exposed 300 Unexposed 600 | UW, FM300, FMHPE | - | -/120/120 | 120 minute | 324 mm x 9.53 mm Steel schedule 40 pipe, with 75 mm thick stone wool insulation. 3 layers of BOSS UniWrap™ wrapped around the insulated pipe section, set back 5 mm from the substrate surface on both sides. BOSS FireMastic-300™ sealant 5 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3247 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3315 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 224 | 16 | - | Exposed 400 Unexposed 600 | FM300, FMHPE | - | -/120/120 | 120 minute | 100 mm x 1.63 mm 'Type B' copper pipe, with 50 mm thick stone wool insulation. BOSS FireMastic-300™ sealant 16 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3248 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3316 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 98 | 16 | 35 | Exposed 300 Unexposed 300 | FMHPE | - | -/120/90 | 120 minute | 25 mm x 1.22 mm 'Type B' copper pipe, with 25 mm thick stone wool insulation. BOSS FireMastic-HPE™ sealant 16 mm deep in annular gap with 35 mm x 35 mm fillet both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3249 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3317 | Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 324 | 324 | 324 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS UniWrap™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 486 | 5 | - | Exposed 300 Unexposed 900 | UW, FMHPE | - | -/90/90 | 90 minute | 324 mm x 9.53 mm Steel schedule 40 pipe, with 75 mm thick stone wool insulation. 3 layers of BOSS UniWrap™ wrapped around the insulated pipe section, set back 5 mm from the substrate surface on both sides. BOSS FireMastic-HPE™ sealant 5 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3250 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3318 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 224 | 16 | 35 | Exposed 400 Unexposed 400 | FMHPE | - | -/120/60 | 120 minute | 100 mm x 1.63 mm 'Type B' copper pipe, with 50 mm thick stone wool insulation. BOSS FireMastic-HPE™ sealant 16 mm deep in annular gap with 35 mm x 35 mm fillet both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3251 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3319 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128 | None | NA | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 98 | 16 | - | Exposed 300 Unexposed 400 | FM300, FMHPE | - | -/120/120 | 120 minute | 25 mm x 1.22 mm 'Type B' copper pipe, with 25 mm thick stone wool insulation. BOSS FireMastic-300™ sealant 16 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-001 Issue 2 | - | 2019-06-04 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3252 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3320 | Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 324 | 324 | 324 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS Batt™ | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | 486 | 5 | - | Exposed 300 Unexposed 600 | BB, UW, FM300, FMHPE | - | -/120/120 | 120 minute | 324 mm x 9.53 mm Steel schedule 40 pipe, with 75 mm thick stone wool insulation. 680 mm x 680 mm section of BOSS Batt™ installed to the top side of the floor system. 3 layers of BOSS UniWrap™ wrapped around the insulated pipe section, set back 5 mm from the substrate surface on both sides. BOSS FireMastic-300™ sealant 5 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3253 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3321 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 224 | 16 | 35 | Exposed 400 Unexposed 600 | FMHPE | - | -/120/90 | 120 minute | 100 mm x 1.63 mm 'Type B' copper pipe, with 50 mm thick stone wool insulation. BOSS FireMastic-HPE™ sealant 16 mm deep in annular gap with 35 mm x 35 mm fillet both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3254 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3322 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 98 | 16 | 35 | Exposed 300 Unexposed 300 | FMHPE | - | -/120/120 | 120 minute | 25 mm x 1.22 mm 'Type B' copper pipe, with 25 mm thick stone wool insulation. BOSS FireMastic-HPE™ sealant 16 mm deep in annular gap with 35 mm x 35 mm fillet both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3255 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3323 | Metal_Pipes | Insulated Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 324 | 324 | 324 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS UniWrap™ | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | 486 | 5 | - | Exposed 300 Unexposed 900 | UW, FM300, FMHPE | - | -/120/120 | 120 minute | 324 mm x 9.53 mm Steel schedule 40 pipe, with 75 mm thick stone wool insulation. 3 layers of BOSS UniWrap™ wrapped around the insulated pipe section, set back 5 mm from the substrate surface on both sides. BOSS FireMastic-300™ sealant 5 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3256 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3324 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 100 | 100 | 100 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 224 | 16 | - | Exposed 400 Unexposed 400 | FM300, FMHPE | - | -/120/60 | 120 minute | 100 mm x 1.63 mm 'Type B' copper pipe, with 50 mm thick stone wool insulation. BOSS FireMastic-300™ sealant 16 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3257 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3325 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Floor | 125 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 125 | None | NA | BOSS FireMastic-300™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 98 | 16 | - | Exposed 300 Unexposed 400 | FM300, FMHPE | - | -/120/120 | 120 minute | 25 mm x 1.22 mm 'Type B' copper pipe, with 25 mm thick stone wool insulation. BOSS FireMastic-300™ sealant 16 mm deep in annular gap both sides. BOSS FireMastic-HPE™ sealant applied 10 mm deep where the insulation finishes at its junction with the pipe on both sides. | FP10422-002 Issue 2 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3258 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3326 | Power_Cables_Inc_Bundles_and_Trays | Appendix D1 Config | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Concrete 400 x 600 and Batt 325 x 70 | 50 | - | 600 | BB, FM300, TDW | - | -/120/90 | 120 minute | Appendix D1 Group A cable configuration, consisting of: - 1 x single core 630 mm² cable - 1 x 3C+E 185 mm² cable - 3 x 3C+E 6 mm² cables - 8 x 3C+E 16 mm² cables 400 mm x 600 mm aperture in the concrete slab protected with 2 layers of BOSS Batt™. Cables installed to a 300 mm wide cable tray penetrating a 325 mm x 70 mm aperture through the BOSS Batt™. BOSS FireMastic-300™ sealant 50 mm deep in the annular gap, flush with the top side. The cable tray and services were wrapped to 600 mm with BOSS Thermal Defence Wrap™ on the top side. | 147114.00 FRT V3.0 | - | 2025-01-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3259 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3327 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | Concrete 400 x 600 and Batt 185 x 125 | 50 | - | 600 | BB, FM300, TDW | - | -/120/120 | 120 minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables 400 mm x 600 mm aperture in the concrete slab protected with 2 layers of BOSS Batt™. Cables installed to a 150 mm wide cable tray penetrating a 185 mm x 125 mm aperture through the BOSS Batt™. BOSS FireMastic-300™ sealant 50 mm deep in the annular gap, flush with the top side. The cable tray and services were wrapped to 600 mm with BOSS Thermal Defence Wrap™ on the top side. | 147114.00 FRT V3.0 | - | 2025-01-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3260 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3328 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 30 | Full depth | - | - | BB, FMHPE | - | -/120/60 | 120 minute | Bundle of 4 x 2.5 mm², 2C+E TPS Power Cables. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3261 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3329 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 30 | Full depth | 20 (1 side only) | - | BB, FMHPE | - | -/120/60 | 120 minute | Bundle of 4 x CAT6 cables. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. A 20 mm x 20 mm fillet of BOSS FireMastic-HPE™ sealant applied to either the exposed or unexposed side. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3262 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3330 | Data_Comms_Cables_Inc_Bundles_and_Trays | COAX | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 30 | Full depth | - | - | BB, FMHPE | - | -/120/90 | 120 minute | Bundle of 4 x COAX cables. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3263 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3331 | Data_Comms_Cables_Inc_Bundles_and_Trays | Fire Alarm | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 30 | Full depth | - | - | BB, FMHPE | - | -/120/90 | 120 minute | Bundle of 4 x Fire Alarm cables. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3264 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3332 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 40 | Full depth | - | - | BB, FMHPE | - | -/120/60 | 120 minute | 20 mm PEX-a pipe with 3.0 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Capped/Capped | BF-3265 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3334 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 46 | Full depth | - | - | BB, FMHPE | - | -/120/60 | 120 minute | 25 mm uPVC pipe with 2.0 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3266
BF-3335 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 54 | Full depth | - | - | BB, FMHPE | - | -/120/90 | 120 minute | 32 mm uPVC pipe with 2.1 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3267
BF-3336 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 63 | Full depth | - | - | BB, FMHPE | - | -/120/60 | 120 minute | 40 mm uPVC pipe with 2.1 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3268
BF-3337 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 75 | Full depth | - | - | BB, FMHPE | - | -/120/15 | 120 minute | HVAC Bundle: - 1 x 3/8" + 5/8" Paircoil with 19 mm thick nitrile rubber insulation - 1 x 2.5 mm² 2C+E TPS Power Cable - 1 x 1.5 mm² control cable BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3269 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3338 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 60 | Full depth | - | - | BB, FMHPE | - | -/120/15 | 120 minute | 50NB Galvanised steel sprinkler pipe with 3.3 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3270 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3339 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 30 | Full depth | - | - | BB, FMHPE | - | -/120/15 | 120 minute | 1 x 16 mm² 2C+E mains cable. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3271 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3340 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/120/90 | 120 minute | Control joint. 1 strip of 100 mm wide BOSS Batt™ installed over a joint in the main BOSS Batt™ substrate, each side of the wall. Cut edges to be coated with layer of BOSS Ablative Coating™. The batt strips were fixed to the separating element with 90 mm pigtail screws, approximately 25 mm from the top and bottom edge of the batt strip, at 300 mm centres. | 148412.00 FTRR V3.0 | - | 2024-07-21 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3272 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3341 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/120/120 | 120 minute | Control joint. 1 strip of 100 mm wide BOSS Batt™ installed over a joint in the main BOSS Batt™ substrate on the exposed side. Cut edges to be coated with layer of BOSS Ablative Coating™. The batt strips were fixed to the separating element with 90 mm pigtail screws, approximately 25 mm from the top and bottom edge of the batt strip, at 300 mm centres. | 148412.00 FTRR V3.0 | - | 2024-07-21 | 2029-09-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3273 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3342 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/120/120 | 120 minute | Control joint. 1 strip of 100 mm wide BOSS Batt™ installed over a joint in the main BOSS Batt™ substrate on the unexposed side. Cut edges to be coated with layer of BOSS Ablative Coating™. The batt strips were fixed to the separating element with 90 mm pigtail screws, approximately 25 mm from the top and bottom edge of the batt strip, at 300 mm centres. | 148412.00 FTRR V3.0 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3274 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3343 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/60/60 | 60 minute | Vertical linear gap seal. A 90 mm x 45 mm timber stud with BOSS Batt™ butting up either side. BOSS Ablative Coating™ to all cut edges of the BOSS Batt™. BOSS Ablative Coating™ between the timber stud and the BOSS Batt™ to seal the junction on both sides. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3275 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3344 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/60/30 | 60 minute | Vertical linear gap seal. A 64 mm steel stud with BOSS Batt™ butting up either side. BOSS Ablative Coating™ to all cut edges of the BOSS Batt™. BOSS Ablative Coating™ between the steel stud and the BOSS Batt™ to seal the junction on both sides. BOSS Ablative Coating™ to exposed faces of the steel stud. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3276 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3345 | NA | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | - | - | - | - | - | - | - | - | - | BB, AC | - | -/60/15 | 60 minute | Vertical linear gap seal. A 64 mm steel stud with BOSS Batt™ butting up either side. BOSS Ablative Coating™ to all cut edges of the BOSS Batt™. BOSS Ablative Coating™ between the steel stud and the BOSS Batt™ to seal the junction on both sides. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3277 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3346 | Other | GPO | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard on each side | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Intumescent Flush Pad | - | - | - | - | - | - | 110 x 53 | - | - | - | IFP | - | -/60/45 | 60 minute | 110 mm high x 53 mm wide steel wallbox with switch, installed within a 110 mm high x 53 mm aperture to the exposed side of the wall system. The wallbox incorporated 4 mm thick x 70 mm long x 40 mm wide BOSS Intumescent Flush Pad friction fitted to the back of the wallbox. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3278 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3347 | Other | GPO | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard on each side | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Intumescent Flush Pad | - | - | - | - | - | - | 110 x 53 | - | - | - | IFP | - | -/60/60 | 60 minute | 110 mm high x 53 mm wide steel wallbox with switch, installed within a 110 mm high x 53 mm aperture to the unexposed side of the wall system. The wallbox incorporated 4 mm thick x 70 mm long x 40 mm wide BOSS Intumescent Flush Pad friction fitted to the back of the wallbox. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3279 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3348 | Other | GPO | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard on each side | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | None | NA | BOSS Intumescent Flush Pad | - | - | - | - | - | - | 110 x 53 | - | - | - | IFP | - | -/60/60 | 60 minute | 110 mm high x 53 mm wide steel wallbox with switch, installed within a 110 mm high x 53 mm aperture in a back-to-back configuration. The wallbox incorporated 4 mm thick x 70 mm long x 40 mm wide BOSS Intumescent Flush Pad friction fitted to the back of the wallbox. | 148597.00 FTR V3.1 | - | 2024-10-17 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3280 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3349 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 - 40 | 20 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 70, 100, 135 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | 3 insulated copper pipes installed directly above one another with the insulation abutting. The pipes include: • 20 mm Copper Pipe with 19 mm Nitrile Rubber insulation through 70 mm aperture. • 32 mm Copper Pipe with 25 mm Nitrile Rubber insulation through 100 mm aperture. • 40 mm Copper Pipe with 38 mm Nitrile Rubber insulation through 135 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3281 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3350 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 120, 120, 120 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | 3 insulated copper pipes installed directly above one another with the insulation abutting. The pipes include: • 3 x 32 mm Copper Pipes with 38 mm Nitrile Rubber insulation, each penetrating 120 mm apertures. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3282 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3351 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 120, 120, 120 | 26 | - | - | FMHPE | - | -/120/45 | 120 minute | 3 insulated copper pipes installed directly beside one another with the insulation abutting. The pipes include: • 3 x 32 mm Copper Pipes with 25 mm Nitrile Rubber insulation, each penetrating 100 mm apertures. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3283 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3352 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 140 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | HVAC Bundle: • 2 sets of 19.05 mm + 9.52 mm copper pipes with 19 mm thick nitrile rubber insulation penetrating a 140 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2024-07-21 | - | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3284 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3353 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 100 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | 15 mm copper pipe with 38 mm thick nitrile rubber insulation penetrating a 100 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3285 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3354 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 60 | 60 | 60 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 160 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | 60 mm copper pipe with 38 mm thick nitrile rubber insulation penetrating a 160 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148815.00 FTR V2.0 | - | 2020-06-15 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3286 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3355 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 138 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 32 mm copper pipe with 38 mm thick nitrile rubber insulation penetrating a 138 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3287 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3356 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 95 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 15 mm copper pipe with 25 mm thick nitrile rubber insulation penetrating a 95 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3288 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3357 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 112 | 26 | - | - | FMHPE | - | -/120/90 | 120 minute | 32 mm copper pipe with 25 mm thick nitrile rubber insulation penetrating a 112 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3289 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3358 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 73 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 15 mm copper pipe with 19 mm thick nitrile rubber insulation penetrating a 73 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3290 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3359 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 28 | 28 | 28 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 96 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 28 mm copper pipe with 19 mm thick nitrile rubber insulation penetrating a 96 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3291 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3360 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 78 | 26 | - | - | FMHPE | - | -/120/60 | 120 minute | 32 mm copper pipe with 13 mm thick nitrile rubber insulation penetrating a 78 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3292 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3361 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 15 | 15 | 15 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 61 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 15 mm copper pipe with 13 mm thick nitrile rubber insulation penetrating a 61 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3293 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3362 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 116 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 32 mm copper pipe with 32 mm thick nitrile rubber insulation penetrating a 116 mm aperture. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | 148816.00 FTR V2.0 | - | 2025-01-22 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3294 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3363 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | BOSS MaxiCollar™ | - | - | - | 5 to 20 | 50 | Full depth | - | - | BB, FMHPE, MC | MC100 Shell | -/120/30 | 120 minute | Bundle of: • 8 x 2.5 mm², 2C+E TPS Power Cables • 8 x CAT6 cables BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap (ranging from 5-20 mm) to the full depth of the BOSS Batt™ flush with the surface. 100 mm BOSS MaxiCollar™ (Shell only) installed on the unexposed side, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush. | 148817.00 FTR V2.1 | - | 2024-07-21 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3295 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3364 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | 5 to 20 | 30 | Full depth | - | - | BB, FMHPE | - | -/120/30 | 120 minute | Bundle of 4 x CAT6 cables. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap (ranging from 5-20 mm) to the full depth of the BOSS Batt™ flush with the surface. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3296 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3365 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | 3 to 10 | 65 | Full depth | - | - | BB, FM300, TDW | - | -/120/30 | 120 minute | 50NB Galvanised steel sprinkler pipe with 3.3 mm wall thickness. BOSS FireMastic-300™ sealant installed on both sides of the wall to fill the annular gap (ranging from 3-10 mm) to the full depth of the BOSS Batt™ flush with the surface. The pipe wrapped to 300 mm with BOSS Thermal Defence Wrap™ on the unexposed side. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3297 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3366 | Metal_Pipes | Sprinkler pipe | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 65 | Full depth | - | - | BB, FM300, TDW | - | -/120/30 | 120 minute | 50NB Galvanised steel sprinkler pipe with 3.3 mm wall thickness. BOSS FireMastic-300™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. The pipe wrapped to 300 mm with BOSS Thermal Defence Wrap™ on the exposed side. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3298 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3367 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | BOSS MaxiCollar™ | - | - | - | - | 50 | Full depth | - | - | BB, FMHPE, MC | MC50 Shell | -/120/15 | 120 minute | Bundle of: • 8 x 2.5 mm², 2C+E TPS Power Cables • 8 x CAT6 cables BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. 50 mm BOSS MaxiCollar™ (Shell only) installed on the unexposed side, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3299 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3368 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 120 | Full depth | - | - | BB, FMHPE | MC100 | -/30/30 | <60 minute | HVAC Bundle: • 1 x 20 mm + 25 mm Paircoil with 19 mm thick nitrile rubber insulation • 1 x 2.5 mm² 2C+E TPS Power Cable • 1 x 1.5 mm² control cable • 1 x 20 mm uPVC condensate drain BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap (ranging from 5-25 mm) to the full depth of the BOSS Batt™ flush with the surface. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3300 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3369 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 45 | Full depth | - | - | BB, FMHPE | - | -/30/30 | <60 minute | 25 mm PEX-a pipe with 2.8 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3301 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3370 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 40 | Full depth | - | - | BB, FMHPE | - | -/120/30 | 120 minute | 20 mm PEX-AL-PEX pipe with 2.2 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148817.00 FTR V2.1 | - | TBC | TBC | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3302 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3371 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 75 | Full depth | - | - | BB, FMHPE | - | -/60/60 | 60 minute | 50 mm uPVC pipe with 2.0 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3303
BF-3372 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 45 | Full depth | 20 | - | BB, FMHPE | - | -/60/45 | 60 minute | 25 mm PEX-a pipe with 2.8 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. A 20 mm x 20 mm fillet of BOSS FireMastic-HPE™ sealant applied to the exposed side only. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3304 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3373 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 25 | 25 | 25 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 45 | Full depth | 20 | - | BB, FMHPE | - | -/120/45 | 120 minute | 25 mm PEX-a pipe with 2.8 mm wall thickness. BOSS FireMastic-HPE™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. A 20 mm x 20 mm fillet of BOSS FireMastic-HPE™ sealant applied to the unexposed side only. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3305 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3374 | Metal_Pipes | Insulated Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS Thermal Defence Wrap | - | - | - | - | 75 | - | - | - | BB, FM300, TDW | - | -/120/30 | 120 minute | 50 mm copper pipe. BOSS FireMastic-300™ sealant installed on both sides of the wall to fill the annular gap to the full depth of the BOSS Batt™ flush with the surface. The service is wrapped with 600 mm of BOSS Thermal Defence Wrap™. The wrap is installed from 1 side and moved down the pipe to position centrally in the substrate, with 275 mm exposed on both sides of the BOSS Batt™. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3306 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3375 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | - | - | - | - | BB, AC, FM300 | - | -/120/90 | 120 minute | BOSS Batt™ to plasterboard substrate infill - Protected steel. Single layer of BOSS Batt™ friction fitted centrally within the 1600 mm x 600 mm aperture, with the steel framing of the plasterboard substrate protected by 1 layer of 13 mm plasterboard. Batt-to-Batt joins were sealed with BOSS Ablative Coating, with Batt edge to interface with the plasterboard substrate, sealed with BOSS FireMastic-300™. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3307 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3376 | NA | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 50 mm BOSS Batt™ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | 50 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-300™ | - | - | - | - | - | - | - | - | BB, AC, FM300 | - | -/120/60 | 120 minute | BOSS Batt™ to plasterboard substrate infill - Exposed steel. Single layer of BOSS Batt™ friction fitted centrally within the 1600 mm x 600 mm aperture, with the steel framing of the plasterboard substrate exposed. Batt-to-Batt joins were sealed with BOSS Ablative Coating, with Batt edge to interface with the steel framing, sealed with BOSS FireMastic-300™. | 148817.00 FTR V2.1 | - | TBC | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3308 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3377 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 8.2 to 15.6 | 127.1 | 26 | 15 | - | FMHPE | - | -/120/120 | 120 minute | HVAC Bundle: • 1 x 19.05 mm + 9.52 mm Paircoil with 19 mm thick nitrile rubber insulation • 1 x 2.5 mm² 3C+E TPS Power Cable • 1 x 1.5 mm² control cable • 1 x 20 mm uPVC condensate drain BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap with 15 mm x 15 mm fillet of sealant applied both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3309 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3378 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.3 to 10.6 | 137.5 | Depth of collar | - | - | MC, FMHPE | MC125 Shell | -/120/120 | 120 minute | HVAC Bundle: • 1 x 32 mm + 25 mm Paircoil with 19 mm thick nitrile rubber insulation • 1 x 2.5 mm² 2C+E TPS Power Cable • 1 x 1.5 mm² control cable • 1 x 25 mm uPVC condensate drain 125 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3310 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3379 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 5.1 to 12.9 | 140.6 | Depth of collar | - | - | MC, FMHPE | MC150 Shell | -/120/120 | 120 minute | HVAC Bundle: • 2 x 19.05 mm + 9.52 mm Paircoil with 19 mm thick nitrile rubber insulation • 2 x 2.5 mm² 2C+E TPS Power Cable • 2 x 1.5 mm² control cable • 2 x 20 mm uPVC condensate drain 150 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3311 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3380 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 13.7 to 17.9 | 79.8 | 26 | 15 | - | FMHPE | - | -/45/45 | <60 minute | 40 mm cPVC pipe with 3.8 mm wall thickness. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap with 15 mm x 15 mm fillet of sealant applied both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3312 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3381 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 3.5 to 5.0 | 28.9 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 1 - Sided penetration. 20 mm PEX-b pipe with 3.05 mm wall thickness, installed penetrating either side of the wall system, with a 90° bend into the cavity. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3313 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3382 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 4.1 to 6.3 | 40.1 | Depth of collar | - | - | MC, FMHPE | MC50 Shell | -/120/120 | 120 minute | Bundle of 12 x 2.5 mm², 2C+E TPS Power Cables. 50 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3314 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3383 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3.6 to 8.9 | 39.9 | Depth of collar | - | - | MC, FMHPE | MC50 Shell | -/120/120 | 120 minute | Bundle of 20 x CAT6 cables. 50 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3315 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3384 | Power_Cables_Inc_Bundles_and_Trays | Aluminium Core | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | - | - | - | - | FMHPE | - | -/120/120 | 120 minute | 70 mm2 Aluminium 1C AL/PVC/XLPE electrical cable. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush both sides. | PF25015 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3316 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3385 | Data_Comms_Cables_Inc_Bundles_and_Trays | Mixed Comms Bundle | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.1 to 8.6 | 55.3 | Depth of collar | - | - | MC, FMHPE | MC50 Shell | -/120/120 | 120 minute | Bundle of communications cables including: • 8 x COAX cables • 8 x CAT6 cables. 50 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3317 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3386 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 40 | 40 | 40 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.8 to 4.4 | 55.4 | Plasterboard 26 and Depth of collar | - | - | MC, FMHPE | MC50 Shell | -/120/90 | 120 minute | 40 mm cPVC pipe with 3.8 mm wall thickness. 50 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3318 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3387 | Plastic_Pipes | CPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 2.2 to 3.6 | 66 | Depth of collar | - | - | MC, FMHPE | MC65 Shell | -/60/60 | 60 minute | 50 mm cPVC pipe with 5.3 mm wall thickness. 65 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3319 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3388 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 3.2 to 7.5 | 102.4 | Depth of collar | - | - | MC, FMHPE | MC125 Shell | -/120/120 | 120 minute | HVAC Bundle: • 2 x 19.05 mm + 9.52 mm Paircoil with 19 mm thick nitrile rubber insulation • 2 x 2.5 mm² 3C+E TPS Power Cable • 2 x 1.5 mm² control cable • 2 x 20 mm uPVC condensate drain 125 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3320 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3389 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | 1.8 to 5.1 | 153.8 | Depth of collar | - | - | MC, FMHPE | MC150 Shell | -/120/120 | 120 minute | HVAC Bundle: • 2 x 19.05 mm + 9.52 mm Paircoil with 25 mm thick nitrile rubber insulation • 2 x 2.5 mm² 3C+E TPS Power Cable • 2 x 1.5 mm² control cable • 2 x 25 mm uPVC condensate drain 150 mm BOSS MaxiCollar™ (Shell only) installed on both sides, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush both sides. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3321 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3390 | HVAC_Bundles-Lagged Copper,_Condensate_Drain_and_Cables | - | Service Penetration | HVAC | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 2.8 to 12.1 | 112 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 1 - Sided penetration - HVAC Bundle: • 1 x 19.05 mm + 9.52 mm Paircoil with 19 mm thick nitrile rubber insulation • 1 x 2.5 mm² 3C+E TPS Power Cable • 1 x 1.5 mm² control cable • 1 x 25 mm uPVC condensate drain Installed penetrating either side of the wall system, with a 90° bend into the cavity. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3322 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3391 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 2 layers of 13 mm plasterboard both sides | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | 4.1 to 4.7 | 28.8 | 26 | - | - | FMHPE | - | -/120/120 | 120 minute | 1 - Sided penetration - 20 mm PEX-AL-PEX pipe with 2.2 mm wall thickness. Installed penetrating either side of the wall system, with a 90° bend into the cavity. BOSS FireMastic-HPE™ sealant 26 mm deep in annular gap finished flush. | PF25016 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3323 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3392 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | BOSS Thermal Defence Wrap | - | - | - | - | - | 111 | 20 | - | 300 | FMHPE, TDW | - | -/120/120 | 120 minute | Bundle of electrical and communications cables, including: • 10 x 0.75 mm² Fire Alarm cables • 20 x CAT6 cables • 15 x 2.5 mm², 2C+E TPS power cables • 4 x 16 mm² electrical cables • 6 x COAX cables • 70 mm² Aluminimum core electrical cable. 100 mm uPVC pipe cast into the concrete slab, flush with the top and bottom. BOSS FireMastic-HPE™ sealant 20 mm deep in annular gap finished flush with the top. The service wrapped to 300 mm with BOSS Thermal Defence Wrap™ on the top side. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3324 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3393 | NA | NA | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-300™ | - | - | - | - | - | - | 36.8 | 20 | - | - | FM300 | - | -/120/120 | 120 minute | Blank service. 32 mm uPVC pipe cast into the concrete slab, flush with the top and bottom. BOSS FireMastic-300™ sealant 20 mm deep in gap finished flush with the bottom. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3325
BF-3394 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | - | - | - | - | - | 90.2 | Depth of collar | - | - | MC, FMHPE | MC80 Shell | -/120/120 | 120 minute | Bundle of electrical and communications cables, including: • 38 x CAT6 cables • 22 x 2.5 mm², 2C+E TPS power cables 80 mm BOSS MaxiCollar™ (Shell only) installed on the underside, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3326 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3395 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 32 | 32 | 32 | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 36.8 | 20 | - | - | FMHPE | - | -/120/120 | 120 minute | Blank service. 32 mm uPVC pipe cast into the concrete slab, flush with the top and bottom. BOSS FireMastic-HPE™ sealant 20 mm deep in gap finished flush with the bottom. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3184: BF-3327
BF-3396 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS MaxiCollar™ | BOSS FireMastic-HPE™ | BOSS Thermal Defence Wrap | - | - | - | - | 90.2 | Depth of collar | - | 300 | MC, FMHPE, TDW | MC80 Shell | -/120/120 | 120 minute | Bundle of electrical and communications cables, including: • 38 x CAT6 cables • 22 x 2.5 mm², 2C+E TPS power cables 80 mm BOSS MaxiCollar™ (Shell only) installed on the underside, sealed to its full depth with BOSS FireMastic-HPE™ sealant finished flush. The service wrapped to 300 mm with BOSS Thermal Defence Wrap™ on the top side. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3328 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3397 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | - | - | - | - | - | - | 111 | 20 | - | - | FMHPE | - | -/120/90 | 120 minute | Bundle of electrical and communications cables, including: • 10 x 0.75 mm² Fire Alarm cables • 20 x CAT6 cables • 15 x 2.5 mm², 2C+E TPS power cables • 4 x 16 mm² electrical cables • 6 x COAX cables • 70 mm² Aluminimum core electrical cable. 100 mm uPVC pipe cast into the concrete slab, flush with the top and bottom. BOSS FireMastic-HPE™ sealant 20 mm deep in annular gap finished flush with the bottom. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3329 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3398 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS FireMastic-HPE™ | BOSS Thermal Defence Wrap | - | - | - | - | - | 111 | 20 | - | 300 | FMHPE, TDW | - | -/120/120 | 120 minute | Bundle of electrical and communications cables, including: • 10 x 0.75 mm² Fire Alarm cables • 20 x CAT6 cables • 15 x 2.5 mm², 2C+E TPS power cables • 4 x 16 mm² electrical cables • 6 x COAX cables • 70 mm² Aluminimum core electrical cable. 100 mm uPVC pipe cast into the concrete slab, flush with the top and bottom. BOSS FireMastic-HPE™ sealant 20 mm deep in annular gap finished flush with the bottom. The service wrapped to 300 mm with BOSS Thermal Defence Wrap™ on the top side. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3330 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3399 | Power_Cables_Inc_Bundles_and_Trays | Appendix D1 Config | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 400 x 600 | Full depth | 25 | 600 | BB, FM300, TDW | - | -/120/120 | 120 minute | Appendix D1 Group A cable configuration, consisting of: - 1 x single core 630 mm² cable - 1 x 3C+E 185 mm² cable - 3 x 3C+E 6 mm² cables - 8 x 3C+E 16 mm² cables Cables installed on a 300 mm wide cable tray, penetrating a 400 mm x 600 mm aperture, protected using two layers of BOSS Batt™, installed flush with the top of the slab and cut to fit around the services. All edges and joins sealed with BOSS FireMastic-300™, with the annular gap filled full depth and finished flush both sides. A 25 mm x 25 mm fillet applied on the top side. The cable tray and services to be wrapped on the top side for 600 mm with BOSS P40-MAK Wrap™. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3331 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3400 | Data_Comms_Cables_Inc_Bundles_and_Trays | Appendix D2 Config | Service Penetration | Electrical | - | - | - | Floor | 120 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 120 | None | NA | BOSS Batt™ | BOSS FireMastic-300™ | BOSS P40-MAK Wrap™ | - | - | - | - | 400 x 600 | Full depth | 25 | 600 | BB, FM300, TDW | - | -/120/120 | 120 minute | Appendix D2 Group B cable configuration, consisting of 60 x 50 pair telecommunication cables Cables installed on a 150 mm wide cable tray, penetrating a 400 mm x 600 mm aperture in the concrete slab. The penetration is protected using two layers of BOSS Batt™, installed flush with the top of the slab and cut to fit around the services. All edges and joins sealed with BOSS FireMastic-300™. Annular gap filled to the full depth of the batt with BOSS FireMastic-300™, applied flush on both sides. A 25 mm x 25 mm fillet of sealant applied on the top side. The cable tray and services to be also wrapped on the top side for 600 mm with BOSS P40-MAK Wrap™. | PF25031 Rev 2 | - | 2025-07-09 | None | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3332 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3401 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 25 | - | - | - | ALX | - | -/120/- | 120 minute | 29 mm wide × 12 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 25 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3334 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3402 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/30/- | <60 minute | 54 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3335 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3403 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 150 | - | - | - | ALX | - | -/120/120 | 120 minute | 170 mm wide × 100 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 150 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3336 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3404 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 35 | - | - | - | ALX | - | -/240/60 | 240 minute | 53.6 mm wide × 20 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 35 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3337 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3405 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/240/- | 240 minute | 63.6 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3338 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3406 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 75 | - | - | - | ALX | - | -/240/60 | 240 minute | 85 mm wide × 50 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 75 mm wide linear gap, positioned at mid-depth of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3339 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3407 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 25 | - | - | - | ALX | - | -/120/- | 120 minute | 29 mm wide × 12 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 25 mm wide vertical linear gap, positioned nominal 50 mm from the unexposed face of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3340 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3408 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/90/90 | 90 minute | 54 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide vertical linear gap, positioned at mid-depth of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3341 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3409 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 150 | - | - | - | ALX | - | -/120/120 | 120 minute | 170 mm wide × 100 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 150 mm wide vertical linear gap, positioned at mid-depth of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3342 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3410 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 35 | - | - | - | ALX | - | -/180/60 | 180 minute | 53.6 mm wide × 20 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 35 mm wide vertical linear gap, positioned at mid-depth of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3343 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3411 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/60/30 | 60 minute | 63.6 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide vertical linear gap, positioned at mid-depth of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3344 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3412 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 75 | - | - | - | ALX | - | -/240/90 | 240 minute | 85 mm wide × 50 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 75 mm wide vertical linear gap, positioned at mid-depth of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3345 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3413 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 10 | - | - | - | ALX | - | -/120/30 | 120 minute | 12 mm wide × 12 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 10 mm wide linear gap, positioned 35 mm from the unexposed side of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3346 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3414 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/60/- | 60 minute | 54 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide linear gap, positioned 35 mm from the unexposed side of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3347 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3415 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Floor | 250 mm thick AAC floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 100 | - | - | - | ALX | - | -/120/60 | 120 minute | 126 mm wide × 100 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 100 mm wide linear gap, positioned 25 mm from the unexposed side of the floor system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3348 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3416 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 10 | - | - | - | ALX | - | -/60/60 | 60 minute | 12 mm wide × 12 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 10 mm wide vertical linear gap, positioned 35 mm from the exposed side of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3349 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3417 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 25 | - | - | - | ALX | - | -/60/- | 60 minute | 32 mm wide × 12 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 25 mm wide vertical linear gap, positioned 30 mm from the exposed face of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3350 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3418 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 50 | - | - | - | ALX | - | -/30/- | <60 minute | 54 mm wide × 25 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 50 mm wide vertical linear gap, positioned 35 mm from the exposed side of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3351 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3419 | Other | - | Linear Joint | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 250 mm thick AAC wall | - | - | - | 1 | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 250 | None | NA | BOSS FireStrip-ALX™ | - | - | - | - | - | - | 100 | - | - | - | ALX | - | -/120/120 | 120 minute | 126 mm wide × 100 mm deep BOSS FireStrip-ALX™ linear gap seal friction fitted within a 100 mm wide vertical linear gap, positioned 25 mm from the exposed side of the wall system. | FAS190039 R2.0 | - | 2025-04-07 | 2030-04-30 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3352 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3420 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 20 | - | - | - | PP-60, FM300 | PP-60 | -/120/60 | 120 minute | 20 mm blank aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3353 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3421 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 16 | 16 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 20 | - | - | - | PP-60, FM300 | PP-60 | -/60/60 | 60 minute | 16 mm PEX pipe. Pipe installed in a 20 mm aperture, sealed with BOSS PenoPatch™ 60 mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3354 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3422 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 20 | - | - | - | PP-60, FM300 | PP-60 | -/60/30 | 60 minute | Bundle of up to 5 communications cables, including a combination of: • CAT6 cables • 0.75 mm² Fire Alarm cables • Security cables • COAX cables Cable bundle installed in a 20 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3355 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3423 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 20 | - | - | - | PP-60, FM300 | PP-60 | -/60/60 | 60 minute | Bundle of up to 3 communications cables, including a combination of: • CAT6 cables • 0.75 mm² Fire Alarm cables • Security cables • COAX cables Cable bundle installed in a 20 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3356 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3424 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 | - | - | - | PP-60, FM300 | PP-60 | -/60/60 | 60 minute | Bundle of up to 3 x 2.5 mm², 2C+E TPS Power Cables. Cable bundle installed in a 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3357 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3425 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 21 | - | - | - | PP-60, FM300 | PP-60 | -/60/45 | 60 minute | 20 mm PEX-AL pipe. Pipe installed in a 21 mm aperture, sealed with BOSS PenoPatch™ 60 mm on both sides, and also wrapped around the service on both sides for 60 mm along its length. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3358 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3426 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 21 | - | - | - | PP-60, FM300 | PP-60 | -/60/30 | 60 minute | 20 mm PEX pipe. Pipe installed in a 21 mm aperture, sealed with BOSS PenoPatch™ 60 mm on both sides, and also wrapped around the service on both sides for 60 mm along its length. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with Fletcher Insulation Pink Partition 14 (R1.3) Glasswool Batt Insulation. | BF-3359 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3427 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/60/60 | 60 minute | 25 mm x 25 mm blank aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3360 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3428 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/60/30 | 60 minute | Single 5 x 1.5 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3361 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3429 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/60/30 | 60 minute | Single 5 x 1.5 mm², EPR/PO sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3362 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3430 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/120/60 | 120 minute | Single 5 x 1.5 mm², XLPE/EVA sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3363 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3431 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/120/30 | 120 minute | Single 1 x 95 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3364 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3432 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/120/- | 120 minute | Up to 16 mm steel pipe. Pipe installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3365 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3433 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/120/- | 120 minute | Up to 16 mm copper pipe. Pipe installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3366 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3434 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/60/60 | 60 minute | Up to 16 mm PVC conduit. Pipe installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3367 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3435 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 60mm | BOSS FireMastic-300™ | - | - | - | - | - | 25 x 25 | - | - | - | PP-60, FM300 | PP-60 | -/120/30 | 120 minute | Single 1 x 185 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3368 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3436 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/60 | 60 minute | 50 mm x 50 mm blank aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3369 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3437 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/60 | 60 minute | Bundle of 3 - 5 x 1.5 mm², PVC/PVC sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3370 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3438 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/30 | 60 minute | Bundle of 3 - 5 x 1.5 mm², EPR/PO sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3371 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3439 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/60 | 60 minute | Bundle of 3 - 5 x 1.5 mm², XLPE/EVA sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3372 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3440 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/30 | 60 minute | Single 1 x 95 mm², PVC/PVC sheathed power cable. Cable installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3373 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3441 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/- | 60 minute | Up to 16 mm steel pipe. Pipe installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3374 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3442 | Metal_Pipes | Copper Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/- | 60 minute | Up to 16 mm copper pipe. Pipe installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3375 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3443 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/60/30 | 60 minute | Up to 16 mm PVC conduit. Pipe installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3376 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3444 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | As required | To achieve the necessary thickness and FRL rating of the originally tested substrate, the separating element can be built-up on one or both sides by using BOSS Batts or fire-rated plasterboard. | BOSS PenoPatch™ 100mm | BOSS FireMastic-300™ | - | - | - | - | - | 50 x 50 | - | - | - | PP-100, FM300 | PP-100 | -/30/30 | <60 minute | Single 1 x 185 mm², PVC/PVC sheathed power cable. Cable installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm on both sides. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | Where a build up is required, a 20 mm x 20 mm fillet of BOSS FireMastic-300™ is to be applied around the build-up piece. Framed systems - Cavity to be filled with mineral wool Insulation. | BF-3377 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3445 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 20 | - | - | - | PP-60 | PP-60 | -/120/60 | 120 minute | 1 - Sided penetration - Approved from both directions. 20 mm blank aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3378 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3446 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 16 | 16 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | As required | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 20 | - | - | - | PP-60 | PP-60 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. 16 mm PEX pipe. Pipe installed in a 20 mm aperture, sealed with BOSS PenoPatch™ 60 mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3379 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3447 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 20 | - | - | - | PP-60 | PP-60 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of up to 5 communications cables, including a combination of: • CAT6 cables • 0.75 mm² Fire Alarm cables • Security cables • COAX cables Cable bundle installed in a 20 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3380 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3448 | Data_Comms_Cables_Inc_Bundles_and_Trays | CAT | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 20 | - | - | - | PP-60 | PP-60 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of up to 3 communications cables, including a combination of: • CAT6 cables • 0.75 mm² Fire Alarm cables • Security cables • COAX cables Cable bundle installed in a 20 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3381 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3449 | Power_Cables_Inc_Bundles_and_Trays | TPS | Service Penetration | Electrical | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 | - | - | - | PP-60 | PP-60 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of up to 3 x 2.5 mm², 2C+E TPS Power Cables. Cable bundle installed in a 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3382 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3450 | Plastic_Pipes | PEX-AL | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 21 | - | - | - | PP-60 | PP-60 | -/60/45 | 60 minute | 1 - Sided penetration - Approved from both directions. 20 mm PEX-AL pipe. Pipe installed in a 21 mm aperture, sealed with BOSS PenoPatch™ 60 mm at all penetration locations, and also wrapped around the service for 60 mm along its length. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3383 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3451 | Plastic_Pipes | PEX | Service Penetration | Plumbing / Hydraulic / Active Fire | 20 | 20 | 20 | Wall | 1 layer of 13 mm plasterboard both sides | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 21 | - | - | - | PP-60 | PP-60 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. 20 mm PEX pipe. Pipe installed in a 21 mm aperture, sealed with BOSS PenoPatch™ 60 mm at all penetration locations, and also wrapped around the service for 60 mm along its length. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3384 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3452 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. 25 mm x 25 mm blank aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3385 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3453 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Single 5 x 1.5 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3386 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3454 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Single 5 x 1.5 mm², EPR/PO sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3387 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3455 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/120/60 | 120 minute | 1 - Sided penetration - Approved from both directions. Single 5 x 1.5 mm², XLPE/EVA sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3388 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3456 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/120/30 | 120 minute | 1 - Sided penetration - Approved from both directions. Single 1 x 95 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3389 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3457 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. Up to 16 mm PVC conduit. Pipe installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3390 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3458 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 60mm | - | - | - | - | - | - | 25 x 25 | - | - | - | PP-60 | PP-60 | -/120/30 | 120 minute | 1 - Sided penetration - Approved from both directions. Single 1 x 185 mm², PVC/PVC sheathed power cable. Cable installed in a 25 mm x 25 mm aperture protected by BOSS PenoPatch™ 60mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3391 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3459 | Other | - | Blank Seal | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. 50 mm x 50 mm blank aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3392 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3460 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of 3 - 5 x 1.5 mm², PVC/PVC sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3393 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3461 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of 3 - 5 x 1.5 mm², EPR/PO sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3394 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3462 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/60 | 60 minute | 1 - Sided penetration - Approved from both directions. Bundle of 3 - 5 x 1.5 mm², XLPE/EVA sheathed power cables. Cables installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3395 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3463 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Single 1 x 95 mm², PVC/PVC sheathed power cable. Cable installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3396 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3464 | Conduit | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 16 | 0 | 16 | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/60/30 | 60 minute | 1 - Sided penetration - Approved from both directions. Up to 16 mm PVC conduit. Pipe installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3397 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3465 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | BOSS PenoPatch™ 100mm | - | - | - | - | - | - | 50 x 50 | - | - | - | PP-100 | PP-100 | -/30/30 | <60 minute | 1 - Sided penetration - Approved from both directions. Single 1 x 185 mm², PVC/PVC sheathed power cable. Cable installed in a 50 mm x 50 mm aperture protected by BOSS PenoPatch™ 100mm at all penetration locations. | FAS190100 R2.1 | - | 2025-08-18 | 2030-06-30 | AS 1530.4:2014 | AS 4072.1-2005 | - | When the service penetrates and exits the same side of the separating element, a minimum of 200 mm separation in the horizontal orientation and 600 mm in vertical orientation must be maintained. | BF-3398 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3466 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/60 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 1-layer of BOSS Batt™ fixed to the underside, with gaps filled to match the floor profile - all edges coated in Ablative Coating. FireMastic-HPE™ applied around cables to 25 mm depth with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS220037 R1.0 | - | 2022-03-21 | 2027-03-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3399 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3467 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with gaps filled to match the floor profile - all edges coated in Ablative Coating. FireMastic-HPE™ applied around cables to 25 mm depth with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS220037 R1.0 | - | 2022-03-21 | 2027-03-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3400 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3468 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the concrete floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS220037 R1.0 | - | 2022-03-21 | 2027-03-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3401 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3469 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/60/60 | 60 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 1-layer of BOSS Batt™ fixed to the underside, with gaps filled to match the floor profile - all edges coated in Ablative Coating. FireMastic-HPE™ applied around cables to 25 mm depth with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation overlapping a 190 mm concrete-filled block wall (min. FRL -/60/60). Void between wall and ComFlor® 60 filled with ≥120 kg/m³ mineral wool beneath floorbox, and BOSS FlexiCoat-MAK™ at the ComFlor® 60 interface. | BF-3402 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3470 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/60/60 | 60 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the concrete floor from the top side, with cables exiting through the underside. 1-layer of BOSS Batt™ fixed to the underside, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation overlapping a 190 mm concrete-filled block wall (min. FRL -/60/60). Void between wall and ComFlor® 60 filled with ≥120 kg/m³ mineral wool beneath floorbox, and BOSS FlexiCoat-MAK™ at the ComFlor® 60 interface. | BF-3403 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3471 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with gaps filled to match the floor profile - all edges coated in Ablative Coating. FireMastic-HPE™ applied around cables to 25 mm depth with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation overlapping a 190 mm concrete-filled block wall (min. FRL -/60/60). Void between wall and ComFlor® 60 filled with ≥120 kg/m³ mineral wool beneath floorbox, and BOSS FlexiCoat-MAK™ at the ComFlor® 60 interface. | BF-3404 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3472 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the concrete floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation overlapping a 190 mm concrete-filled block wall (min. FRL -/60/60). Void between wall and ComFlor® 60 filled with ≥120 kg/m³ mineral wool beneath floorbox, and BOSS FlexiCoat-MAK™ at the ComFlor® 60 interface. | BF-3405 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3473 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/60/60 | 60 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 1-layer of BOSS Batt™ fixed to the underside, with gaps filled to match the floor profile - all edges coated in Ablative Coating. FireMastic-HPE™ applied around cables to 25 mm depth with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation near intumescent-coated steel beam (structural adequacy ≥120 min). Void between beam flange and ComFlor® 60 filled with ≥120 kg/m³ mineral wool on floorbox side, and BOSS Batt™ on opposing side. | BF-3406 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3474 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/60/60 | 60 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the concrete floor from the top side, with cables exiting through the underside. 1-layer of BOSS Batt™ fixed to the underside, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation near intumescent-coated steel beam (structural adequacy ≥120 min). Void between beam flange and concrete floor filled with ≥120 kg/m³ mineral wool on floorbox side, and BOSS Batt™ on opposing side. | BF-3407 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3475 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | ComFlor® 60 (Composite floor deck), max 130 mm thick to min 70 mm thick. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | 130 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the ComFlor® 60 floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with gaps in floor ribs filled to match the profile of the floor, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation near intumescent-coated steel beam (structural adequacy ≥120 min). Void between beam flange and ComFlor® 60 filled with ≥120 kg/m³ mineral wool on floorbox side, and BOSS Batt™ on opposing side. | BF-3408 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3476 | Other | GPO | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick concrete floor | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 150 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS FireMastic-HPE™ | BOSS FireMastic-300™ | - | - | - | - | 25 | 25 | - | BB, AC, FMHPE, FM300 | - | -/120/120 | 120 minute | Recessed electrical floorbox containing up to three 32 mm diameter cable bundles, including: • Up to 8 × CAT6 cables • Up to 4 × 2C+E PVC-sheathed power cables The floorbox is recessed into the concrete floor from the top side, with cables exiting through the underside. 2-layers of BOSS Batt™ fixed to the underside, with all edges coated in Ablative Coating. FireMastic-HPE™ applied to gaps between the cables and BOSS Batt™ to a depth of 25 mm, finished with a 25 × 25 mm fillet to the underside. FireMastic-300™ to the interface of the BOSS Batt™ and floor system. | FAS230092 R1.0 | - | 2023-05-17 | 2028-05-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Approved for installation near intumescent-coated steel beam (structural adequacy ≥120 min). Void between beam flange and concrete floor filled with ≥120 kg/m³ mineral wool on floorbox side, and BOSS Batt™ on opposing side. | BF-3409 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3477 | Power_Cables_Inc_Bundles_and_Trays | Busbar | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/180/30 | 180 minute | 45 mm x 35 mm Zucchini LB Plus electrical busbar, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3410 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3478 | Power_Cables_Inc_Bundles_and_Trays | Busbar | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/180/30 | 180 minute | 92 mm x 40 mm Zucchini MS electrical busbar, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3411 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3479 | Other | Damper | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 200 mm thick concrete floor with 1400 mm x 700 mm aperture with 105 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | 200 | None | NA | Boss FireMortar-360™ | - | - | - | - | - | - | 1400 x 700 | - | - | - | FM360 | - | -/240/30 | 240 minute | 479 mm long x 452 mm wide x 155 mm high curtain blade damper, penetrating a maximum 1400 mm x 700 mm aperture filled with 105 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the bottom face of the floor. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3412 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3480 | Metal_Pipes | Steel Pipes | Service Penetration | Plumbing / Hydraulic / Active Fire | 75 | 75 | 75 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 600 | FM360, P40MAK | - | -/240/120 | 240 minute | 75 mm steel pipe with 3.2 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 50 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 600 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3413 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3481 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, UW, FM300 | 2 layers of UW-25 | -/120/120 | 120 minute | 50 mm PP pipe with 2.0 mm - 6.9 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 2-layers of BOSS UniWrap™ cast into the BOSS FireMortar-360™ at mid-depth. 10 mm wide x 10 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3414 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3482 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, UW, FM300 | 10 layers of UW-25 | -/120/120 | 120 minute | 200 mm PP pipe with 4.9 mm - 18.2 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 10-layers of BOSS UniWrap™ cast into the BOSS FireMortar-360™ at mid-depth. 10 mm wide x 10 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3415 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3483 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, UW, FM300 | 2 layers of UW-25 | -/120/120 | 120 minute | 50 mm uPVC pipe with 2.4 mm - 3.7 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 2-layers of BOSS UniWrap™ cast into the BOSS FireMortar-360™ at mid-depth. 10 mm wide x 10 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3416 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3484 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS UniWrap™ | - | - | - | - | - | 1400 x 700 | - | - | - | FM360, UW | 10 layers of UW-25 | -/90/90 | 90 minute | 200 mm uPVC pipe with 7.7 mm - 9.6 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 10-layers of BOSS UniWrap™ cast into the BOSS FireMortar-360™ at mid-depth. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3417 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3485 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 200 | 200 | 200 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS UniWrap™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, UW, FM300 | 10 layers of UW-25 | -/120/120 | 120 minute | 200 mm uPVC pipe with 9.6 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 10-layers of BOSS UniWrap™ cast into the BOSS FireMortar-360™ at mid-depth. 10 mm wide x 10 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3418 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3486 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | - | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC | MC110 | -/120/120 | 120 minute | 110 mm PE pipe with 4.2 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 110 mm BOSS MaxiCollar™ installed on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3419 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3487 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC110 | -/120/120 | 120 minute | 110 mm PE pipe with 2.7 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 110 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3420 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3488 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC125 | -/120/120 | 120 minute | 125 mm PE pipe with 3.1 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 125 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3421 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3489 | Plastic_Pipes | PE | Service Penetration | Plumbing / Hydraulic / Active Fire | 160 | 160 | 160 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | - | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC | MC160 | -/120/120 | 120 minute | 160 mm PE pipe with 3.1 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 160 mm BOSS MaxiCollar™ installed on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3422 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3490 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC50 | -/120/120 | 120 minute | 50 mm uPVC pipe with 1.8 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 50 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on both sides. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3423 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3491 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 110 | 110 | 110 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC110 | -/120/120 | 120 minute | 110 mm uPVC pipe with 4.2 - 7.3 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 110 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on both sides. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3424 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3492 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC125 | -/120/120 | 120 minute | 125 mm uPVC pipe with 6.0 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 125 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on both sides. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3425 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3493 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 160 | 160 | 160 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | - | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC | MC160 | -/120/120 | 120 minute | 160 mm uPVC pipe with 9.5 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 160 mm BOSS MaxiCollar™ installed on the underside. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3426 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3494 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 160 | 160 | 160 | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 1400 x 700 | - | - | - | FM360, MC, FM300 | MC160 | -/120/120 | 120 minute | 160 mm uPVC pipe with 6.2 - 9.5 mm maximum wall thickness, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 160 mm BOSS MaxiCollar™ installed on the underside. 10 mm wide x 5 mm deep gap around the service filled with BOSS FireMastic-300™ on both sides. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3427 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3495 | Power_Cables_Inc_Bundles_and_Trays | Cable tray | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/120/120 | 120 minute | 250 mm wide x 125 mm deep x 1.5 mm thick steel cable ladder, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3428 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3496 | Power_Cables_Inc_Bundles_and_Trays | Cable tray | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/120/120 | 120 minute | 450 mm wide x 25 mm high x 1.0 mm thick perforated steel cable tray, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3429 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3497 | Power_Cables_Inc_Bundles_and_Trays | Cable tray | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/90/90 | 90 minute | 350 mm wide x 125 mm deep x 1.5 mm thick steel cable ladder, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3430 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3498 | Power_Cables_Inc_Bundles_and_Trays | Cable tray | Service Penetration | Plumbing / Hydraulic / Active Fire | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/90/90 | 90 minute | 450 mm wide x 25 mm high x 1.0 mm thick unperforated steel cable tray, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3431 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3499 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/120/90 | 120 minute | 1 × 3C+E 185 mm2 PVC or XLPE insulated, PVC sheathed cable, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3432 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3500 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/120/90 | 120 minute | 3 × 3C+E 6 mm2 PVC insulated, PVC sheathed cables, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3433 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3501 | Power_Cables_Inc_Bundles_and_Trays | Multi Core / Orange Circular / Mains | Service Penetration | Electrical | - | - | - | Floor | 150 mm thick AAC floor with 1400 mm x 700 mm aperture with 100 mm thick FM-360 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | - | - | - | - | - | - | - | 150 | None | NA | Boss FireMortar-360™ | BOSS P40-MAK Wrap™ | - | - | - | - | - | 1400 x 700 | - | - | 400 | FM360, P40MAK | - | -/120/90 | 120 minute | 8 × 3C+E 1.6 mm2 PVC insulated, PVC sheathed cables, penetrating a maximum 1400 mm x 700 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar, flush with the top face of the floor. 400 mm length of BOSS P40-MAK Wrap™ installed to the top side of the system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3434 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3502 | Plastic_Pipes | HDPE | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Wall | 2 layers of 12.5 mm plasterboard both sides with 295 mm x 215 mm aperture with 100 mm thick FM-360 | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 295 x 215 | - | - | - | FM360, UW | 4 layers of UW-25 | -/120/120 | 120 minute | 125 mm HDPE pipe with 3.1 mm maximum wall thickness, penetrating a maximum 295 mm x 215 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar. 4-layers of BOSS UniWrap™ installed around the service flush to each face of the wall system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3435 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3503 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Wall | 2 layers of 12.5 mm plasterboard both sides with 295 mm x 215 mm aperture with 100 mm thick FM-360 | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 295 x 215 | - | - | - | FM360, UW | 4 layers of UW-25 | -/120/120 | 120 minute | 125 mm PVC pipe with 4.8 mm maximum wall thickness, penetrating a maximum 295 mm x 215 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar. 4-layers of BOSS UniWrap™ installed around the service flush to each face of the wall system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3436 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3504 | Plastic_Pipes | UPVC | Service Penetration | Plumbing / Hydraulic / Active Fire | 125 | 125 | 125 | Wall | 2 layers of 12.5 mm plasterboard both sides with 295 mm x 215 mm aperture with 100 mm thick FM-360 | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 295 x 215 | - | - | - | FM360, UW | 4 layers of UW-25 | -/120/120 | 120 minute | 125 mm PVC pipe with 7.4 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar. 4-layers of BOSS UniWrap™ installed around the service flush to each face of the wall system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3437 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3505 | Plastic_Pipes | PP | Service Penetration | Plumbing / Hydraulic / Active Fire | 50 | 50 | 50 | Wall | 2 layers of 12.5 mm plasterboard both sides with 295 mm x 215 mm aperture with 100 mm thick FM-360 | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | None | NA | Boss FireMortar-360™ | BOSS MaxiCollar™ | BOSS FireMastic-300™ | - | - | - | - | 295 x 215 | - | - | - | FM360, UW | 4 layers of UW-25 | -/120/120 | 120 minute | 50 mm PP pipe with 3.1 mm maximum wall thickness, penetrating a maximum 295 mm x 215 mm aperture filled with 100 mm thick BOSS FireMortar-360™ gypsum based mortar. 4-layers of BOSS UniWrap™ installed around the service flush to each face of the wall system. | FAS220105 R1.1 | - | 2022-10-13 | 2027-08-31 | AS 1530.4:2014 | AS 4072.1-2005 | - | Tested Uncapped/Capped | BF-3438 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3506 | Other | Steel Purlin | Service Penetration | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 2 layers of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144 | None | NA | BOSS Batt™ | BOSS Ablative Coating™ | BOSS Thermal Defence Wrap | BOSS FireMastic-300™ | - | - | - | 170 x 325 | - | - | - | BB-50, AC, TDW, FM300 | - | -/120/120 | 120 minute | 300 × 100 × 1.45 mm C-Steel Purlin (HST300/15) penetrating two layers of BOSS Batt™ (350 mm × 475 mm) cut to the purlin profile, with one pattress layer on each wall face, protecting a 170 mm × 325 mm aperture. The purlin is to rest on the base of the aperture in the separating element. All batt edges are coated with BOSS Ablative Coating, and BOSS FireMastic-300™ is applied between the batt and substrate and to its edge. Two laminated batts are inserted into the purlin opening, extending 580 mm each side, with FireMastic-300™ between batts and purlin. On each side, 580 mm of BOSS Thermal Defence Wrap (two layers, 300 mm long, 20 mm overlap) is fitted, sealed at the BOSS Batt™ with FireMastic-300™. | PF22053 Rev 2 | - | 2022-10-17 | NA | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3439 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3507 | Other | Timber | Service Penetration | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | FBL-100 Intumescent coating | - | - | - | - | 20 | 85 x 130 | 13 | - | - | FMHPE, FBL-100 | - | 60/60/60 | 60 minute | 90 × 45 mm H1.2 radiata pine penetrates an aperture up to 85 mm wide × 130 mm high. FireMastic-HPE™ is applied to the 20 mm annular gap to a depth of 13 mm on both sides. A 1000 µ DFT patch of FBL-100 Intumescent Coating System (ICS), nominally 245 mm wide × 290 mm high, is applied around the aperture to the exposed side. FBL-100 ICS is also applied to all four sides of the timber at 1000 µ DFT for 300 mm along its length to the exposed side. | PFITS PF 19022 | - | 2019-08-14 | NA | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3440 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3508 | Other | Timber | Service Penetration | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | FBL-100 Intumescent coating | - | - | - | - | 20 | 85 x 130 | 13 | - | - | FMHPE, FBL-100 | - | 60/60/60 | 60 minute | 90 × 45 mm H1.2 radiata pine penetrates an aperture up to 85 mm wide × 130 mm high. FireMastic-HPE™ is applied to the 20 mm annular gap to a depth of 13 mm on both sides. A 1000 µ DFT patch of FBL-100 Intumescent Coating System (ICS), nominally 245 mm wide × 290 mm high, is applied around the aperture to the exposed side. FBL-100 ICS is also applied to all four sides of the timber at 1000 µ DFT for 500 mm along its length to the exposed side. | PFITS PF 19022 | - | 2019-08-14 | NA | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3441 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3509 | Other | Timber | Service Penetration | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | FBL-100 Intumescent coating | - | - | - | - | 20 | 85 x 130 | 13 | - | - | FMHPE, FBL-100 | - | 60/60/60 | 60 minute | 90 × 45 mm H1.2 radiata pine supporting 16 mm thick plywood. The timber framing penetrates an aperture up to 85 mm wide × 130 mm high. FireMastic-HPE™ is applied to the 20 mm annular gap to a depth of 13 mm on both sides. FBL-100 Intumescent Coating System (ICS) is applied at 1000 µ DFT to the following locations on the exposed side: • 245 mm x 190 mm patch, applied around the aperture below the plywood. • Three sides of the timber (not top) for 500 mm along its length. • 100 mm wide on both sides of the the framing on the underside of the plywood for 500 mm along its length. | PFITS PF 19022 | - | 2019-08-14 | NA | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3442 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3510 | Other | Timber | Service Penetration | Construction (Linear Gaps / Blank Seals) | - | - | - | Wall | 1 layer of 13 mm plasterboard both sides | - | 1 | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | None | NA | BOSS FireMastic-HPE™ | FBL-100 Intumescent coating | - | - | - | - | 20 | 85 x 130 | 13 | - | - | FMHPE, FBL-100 | - | 60/60/60 | 60 minute | 90 × 45 mm H1.2 radiata pine supporting 2-layers of 16 mm thick fire rated plasterboard. The timber framing penetrates an aperture up to 85 mm wide × 130 mm high. FireMastic-HPE™ is applied to the 20 mm annular gap to a depth of 13 mm on both sides. FBL-100 Intumescent Coating System (ICS) is applied at 1000 µ DFT to the following locations on the exposed side: • 245 mm x 190 mm patch, applied around the aperture below the plasterboard. • Three sides of the timber (not top) for 300 mm along its length. • 100 mm wide on both sides of the the framing on the underside of the plasterboard for 300 mm along its length. | PFITS PF 19022 | - | 2019-08-14 | NA | AS 1530.4:2014 | AS 4072.1-2005 | - |  | BF-3443 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
BF-3444
BF-3445
Note on P257: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Chad - Discussed with Euan 25th Feb 25, drawing number BF-2257 TO BF 2289 has been developed to show BOSS Batts as the primary infill for oversized apertures and therefore pattress fit on both sides of the wall, for SP, AAC & Pronto we should use columns P, Q & R,. As we will later show drawings for this application where “build up” only on one side of the wall has options for cal sil and PB meaning we’d show the white box with Build up hatching.
Note on BJ764: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Report checked and the collar was only on the exposed side, not unexposed side as the assessment says. The report also doesn’t indicate what material the pipe was.
Note on BJ765: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Report checked and the collar was only on the exposed side, not unexposed side as the assessment says. The report also doesn’t indicate what material the pipe was.
Note on P766: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P767: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P768: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P769: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P770: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P771: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P772: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P773: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup
Note on P774: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When installed directly through wall substrate (no Batt) the systems will include Speedpanel with Buildup